SECTION D 12 – Ventilation & Air-Conditioning

# TECHNICAL SPECIFICATIONS

# C.1	GENERAL

INTRODUCTION

The system includes complete HVAC works for Common areas of Industrial Large/Medium/Small Karkhana units and commercial office building.

1.1	These specifications cover the following types of air-conditioning:

- Central air-conditioning system

Central air-conditioning system included in these specifications is by means of centrifugal/ Screw type compressors.

These Specifications cover the equipment and materials for the system, their testing and/or inspection as may be necessary before their dispatch from their respective works, their delivery at site, all preparatory works, assembling, installation and adjustments, commissioning, final testing, putting in to operation, equipment capacity computation and handing over of the complete system.

1.2	RELATED DOCUMENTS

These Specifications shall be read in conjunction with schematic drawings and other documents connected with the work.

1.3	TERMINOLOGY

The definition of terms used in these specifications shall be in accordance with IS: 3615-"Glossary of terms used in refrigeration and air-conditioning".

1.4	COLOUR SCHEME FOR THE EQUIPMENTS AND COMPONENTS

- Colour scheme for equipment like chilling unit, pumps, AHUs, cooling tower etc. shall be as per manufacturer’s standard colour scheme and approval from Owner/PMC-in-charge.

- The scheme of colour code painting of pipe work services for air conditioning installation shall be as per National building code and is indicated below: -

| Description | Ground Colour | Lettering Colour | First Colour band |
| --- | --- | --- | --- |
| Condenser water piping | Sea Green | Black | French Blue |
| Chilled water piping | Sea Green | Black | Black |
| Drain Pipe | Black | White |  |
| Vent | White | Black |  |
| Valves and pipe line fittings | White with Black Handles | Black |  |
| Belt guard | Black & Yellow diagonal strips |  |  |
| Machine bases, Inertia Base Plinth | Charcoal grey |  |  |

- Colour bands shall be 150mm wide, superimposed on ground colour to distinguish type and condition of fluids. The spacing of band shall not exceed 4.0m.

- In addition to the colour bands specified above all pipe work shall be legibly marked with black or white letters to indicate the type of service and the direction of flow identified as follows:

- Chilled water				:	CHW

- Condenser water			:	CDW

- Condensate 				:	C

1.5	Codes and Regulations

- 1.5.1	The following codes and standards shall be used in the design:

- National Building Codes: Building Services 2016

- The American Society for Heating, Refrigerating, and Air Conditioning Owner/PMCs (ASHRAE) standards:

      - Ventilation for acceptable indoor air quality 62.1-2007.

      - Energy standards for buildings 90.1-2007.

      - ASHRAE handbooks:

      - 2006 ASHRAE Handbook, Refrigeration.

      - 2007 ASHRAE Handbook, Applications.

      - 2008 ASHRAE Handbook, Systems and applications.

      - 2009 ASHRAE Handbook, Fundamentals.

- Air Conditioning, Heating and Refrigeration Institute (AHRI).

- Sheet Metal and Air Conditioning Contractors National Association (SMACNA)

- HVAC duct construction standards, metal and flexible, 1995.

- Energy Conservation Building Code (ECBC 2017)

- ASHRAE 52.1-1992, 52.2-2007.

- IMD Weather Data.

- 1.5.2	The following IS codes shall be applicable for Material/Item of work:

1.	Ducting Fabrication	IS :  655 (Latest Rev.)/ SMACN

2.	Galvanised Sheets/Wires	IS :  277-1977

3.	Aluminium Sheets/Wires	IS :  737

4.	Horizontal Centrifugal Pumps	IS : 1620

5.	Mild Steel, ERW Pipes	IS : 1239,   IS : 3589

6.	Pipe Fittings	IS : 1239

7.	Steel Pipe Flanges	IS : 6392

8.	Gate, Globe and Check Valves

a)	Upto 40 mm gun metal	IS :  778

b)	Butterfly valves of 50 mm and above

(cast iron)	IS :  780,  IS : 2906

c)	Balancing Valves 	IS :  778

d)	Non Return Valves	IS : 5312

9.	Colour Code for Identifications of pipes	IS : 2379-1963

10.	3 Phase induction motors	IS :  325

11.	Burden type pressure gauges	IS : 3624

12.	PVC insulated electric cables	IS : 1554

13.	HRC cartridge fuse links	IS : 2208

14.	Starters sheets/wires	IS : 8555

15.	Specific requirements for

direct switching of motors	IS : 4064 (Part II)

16.	Inspection and testing of Installation	IS :  732 (Part III)

17.	Glossary of terms used in refrigeration and

air-conditioning	IS : 3615

18.	Hot die zinc coated steel pipes	IS : 4736-1968

19.	Expanded polystyrene	IS : 4671

20.	Glass wool	IS : 8183

21.	Resin bonded glass wool	IS : 8183

1.5.3 Safety codes

The following safety codes as laid down by ISI shall be followed:

- Safety code for mechanical refrigeration	IS :  660

- Safety code for air-conditioning	IS :  659

- Safety code for scaffolding and ladders	IS : 3696

- Code for practice for safety and health

requirements in electrical and gas

welding and cutting operations             	IS : 3696

- Code of safety procedures and practices

in electrical works	IS : 5216

# C.2	CENTRAL AIR CONDITIONING PLANT - WATER CHILLING MACHINE

C.2.1	MAGNETIC CENTRIFUGAL WATER CHILLING MACHINE (AHRI Certified) (Origin: USA/Europe)

2.1.1	SCOPE

The scope of this section consists of but is not necessarily limited to the following:

a.	Design, Manufacture and supply of centrifugal liquid chillers using Refrigerant- HFC 134 with associated   motors,  starter and accessories.  Chillers shall have no more than two oil-free, magnetic bearing, semi-hermetic centrifugal compressors (no exceptions). Each compressor shall have an integrated variable-frequency drive operating in concert with inlet guide vanes for optimized full and part load efficiency. On two-compressor units, the evaporator and condenser refrigerant sides and the expansion valve shall be common and the chiller shall be capable of running on one compressor with the other compressor or any of its auxiliaries inoperable or removed. Unit shall be refrigerant charged at factory and then dispatched.

b.	All associated items herein to be supplied delivered and installed.

c.	Assembly of chiller components including connection  of cooler, condenser, motor, compressor, VFD, Control panel etc. into complete refrigeration machine. Complete assembled machine in all respect shall be tested prior to dispatch.

d.   	Provide manufacturer’s factory representative’s services, including coordination, and start-up   and erection & testing supervision.

e.	The chiller shall be witness tested at manufacturer's work at 100%,75%,50%,25% at reducing condenser water temperature as per AHRI 550-590 std on AHRI certified test bed. Testing charges, travel, lodging, boarding charges for 4 persons shall be included in the scope.

2.1.2	QUALITY ASSURANCE PROGRAMME

a.	Chiller shall be rated in accordance with Parameters indicated in Technical Specifications.  Pressure vessels shall be designed, constructed, tested, stamped and shall be complete   with safety devices   in accordance   with ANSI/ASHRAE  15-1989 Safety Code and ASME Code.

b.	Chiller manufacturer plant shall be ISO 9001 and 14001 Certified

c.	The chiller shall be designed/manufactured and tested in accordance with the applicable portions of the latest revisions of the following Standards and Codes.

|  | AHRI 550/590 | - | Performance rating of water chilling packages using the vapour compression cycle. |  |
| --- | --- | --- | --- | --- |
|  | ANSI/ASHRAE 15 | - | Reducing the Release of Halogenated Refrigerants from Refrigerating and Air-Conditioning Equipment and Systems |  |
|  | ASHRAE Standard 90.1 | - | Energy Standard for Buildings, Except Low-Rise Residential Buildings |  |
|  | AHRI 575 | - | Air Conditioning and Refrigeration Institute. Standard Method of Measuring Machinery Sound Within Equipment Rooms (Basis of all data presented or field testing of equipment, with relation to sound requirements). |  |
|  | ASME CODE | - | American Society of Mechanical Owner/PMCs. (Div. 1 Code for Unfired Pressure Vessels - Section VIII, Design, construction, testing and certification of pressure vessels)/ equivalent. |  |
|  | ETL | - | Chiller should be complied with ETL Code & Standard |  |

2.1.3	CAPACITY

Actual refrigeration capacity of chilling machine shall be as per actual calculations, Technical Specification and approval from Owner/PMC-in-charge.

    - 2.1.4	CENTRIFUGAL COMPRESSOR

- The unit shall utilize magnetic bearing, oil-free, semi- hermetic centrifugal compressors. The compressor drive train shall be capable of coming to a controlled, safe stop in the event of a power failure. The motor shall be of the semi-hermetic type, of sufficient size to efficiently fulfil compressor horsepower requirements. It shall be liquid refrigerant cooled with internal thermal sensing devices in the stator windings. The motor shall be designed for variable frequency drive operation.

- If the compressor design requires a shaft seal to contain the refrigerant, the manufacturer shall supply a 20 year parts and labour warranty on the shaft seal and a lifetime refrigerant replacement warranty if a seal failure leads to refrigerant loss.

- The chiller shall be equipped with a refrigerant or air cooled integrated Variable Frequency Drive (VFD) to automatically regulate compressor speed in response to cooling load and the compressor pressure lift requirement. Movable inlet guide vanes and variable compressor speed, shall provide unloading. The chiller controls shall coordinate compressor speed and guide vane position to optimize chiller efficiency.

- Each compressor circuit shall be equipped with a 5%-line reactor to help protect against incoming power surges and help reduce harmonic distortion. THID level shall be ≤ 30% at chiller.

    - Capacity Control & Microprocessor Control Centre

at	The unit shall have a microprocessor-based control system consisting of a ≥15-inch VGA touch-screen operator interface and a unit controller.

b	The touch-screen shall display the unit operating parameters, accept setpoint changes (multi-level password protected) and be capable of resetting faults and alarms. The following parameters shall be displayed on the home screen and also as trend curves on the trend screen:

        - Entering and leaving chilled and condenser water temperatures

        - Evaporator and condenser saturated refrigerant pressures

        - Percent of 100% speed (per compressor)

        - % of rated load amps for entire unit

c	in addition to the trended items above, all other important real-time operating parameters shall also be shown on the touch-screen. These items shall be displayed on a chiller graphic showing each component. At a minimum, the following critical areas must be monitored:

d	Compressor actual speed, maximum speed, percent speed Evaporator water in and out temperatures, refrigerant pressure and temperature

        - Condenser water in and out temperatures, refrigerant pressure and temperature

        - Liquid line temperature

        - Chilled water setpoint

        - Compressor and unit state and input and output digital and analog values

e	A fault history shall be displayed using an easy to decipher, colour coded set of messages that are date and time stamped. The alarm history shall be downloadable from the unit’s USB port. An operating and maintenance manual specific for the unit shall be viewable on the screen and downloadable.

f	All setpoints shall be viewable and changeable (multi- level password protected) on the touch screen and include setpoint description and range of set values.

g	Automatic corrective action to reduce unnecessary cycling shall be accomplished through preemptive control of low evaporator or high discharge pressure conditions to keep the unit operating through abnormal transient conditions.

h	The factory mounted controller shall support operation on Modbus RTU for integrating with Building Automation System (BAS) supplier.

i	The chiller shall be able to maintain operation during a momentary power loss event lasting up to 5 seconds when operated at standard AHRI load and lift conditions. The chiller shall be able to ride through this momentary power loss event without shutting down. Chillers not able to maintain operation during momentary power loss events lasting up to 5 seconds shall include a thermal storage tank (seized equivalent to 15 minutes’ requirement) to maintain temperature stability in the system.

The compressor shall be equipped with an automatic suction   damper or inlet guide vanes   control   in combination with VFD for regulating its capacity. Priority will be given to VFD for reducing speed of motor to maximize efficiency.  The positioning of the damper / guide vanes   shall be done by means of thermostatically actuated electronic temperature-controller differential-type with its sensing element or elements in the outgoing chilled water lines.   The automatic damper / guide vanes will maintain the constant temperature of chilled water.   It should be possible to go down from 100% to 10%. at reducing condenser temp. conditions. Necessary safety mechanisms such as chilled water temperature modulation shall be incorporated to keep machine in operating zone at constant entering condenser water temperature conditions.

2.1.8	EVAPORATOR AND CONDENSER

a	Provide sufficient isolation valves and condenser volume to hold the full unit refrigerant charge in the condenser during servicing or provide a separate pumpout system and storage tank sufficient to hold the charge of the largest unit being furnished.

b	The evaporator and condenser shall be separate vessels of the shell-and-tube type, designed, constructed, tested and stamped according to the requirements of the ASME Code, Section VIII. The tubes shall be individually replaceable and secured to the intermediate supports without rolling.

c	The evaporator shall be flooded type with copper tubes rolled into carbon steel tube sheets. The evaporator shall have right-hand connections when looking at the unit control panel.  Water connections shall be grooved suitable for Victaulic couplings. The heads shall be carbon steel and the tube sheets shall be carbon steel. The waterside shall be designed for a minimum of 150psig. The wall copper tubes shall be 0.025 in. Pressure drop in evaporator shall not exceed 6.5 metre.

d	The condenser shall have rolled tube sheets. The condenser shall have right-hand connections when looking at the unit control panel. The condenser shall be equipped with marine water boxes with removable covers and vent and drain connections. Water connections shall be grooved suitable for Victaulic couplings. The heads shall be carbon steel and the tube sheets shall be carbon steel. The wall copper tubes shall be 0.025 in. The waterside shall be designed for a minimum of 150psig. Pressure drop in condenser shall not exceed 6.5 metre.

e	An electronic expansion valve shall control refrigerant flow to the evaporator. Fixed orifice devices or float controls with hot gas bypass are not acceptable because of inefficient control at low load conditions. The liquid line shall have moisture indicating sight glass.

f	Re-seating type spring loaded pressure relief valves according to ASHRAE-15 safety code shall be furnished. The evaporator shall be provided with single or multiple valves. The condenser shall be provided with dual relief valves equipped with a transfer valve so one relief valve can be removed for testing or replacement without loss of refrigerant or removal of refrigerant from the condenser. Rupture disks are not acceptable.

g	The evaporator vessel, including suction line and any other component or part of a component subject to condensing moisture (excluding the waterbox), shall be insulated with 3/4 inch closed cell insulation. All joints and seams shall be carefully sealed to form a vapor barrier.

i	The evaporator waterbox shall be insulated with ¾ inch closed cell insulation.  All joints and seams shall be carefully sealed to form a vapor barrier.

j	Provide neoprene waffle-type vibration isolators for each corner of the unit

k	Power connection shall be single-point

2.1.9	INSTALLATION

The chilling machine shall be installed over a cement concrete platform and shall be adequately isolated as per manufacturers recommendations against transmission of vibrations to the building structure.

2.1.12	PAINTING

Centrifugal water chilling machine shall be finished with durable enamel paint. Shop coats of paint that have become marred during shipment or erection, shall be cleaned off with mineral spirits, wire brushed and spot primed over the affected areas, then coated with enamel paint to match the finish over the adjoining shop-painted surface.

2.1.13	PERFORMANCE RATING

The unit shall be selected for the lowest operating noise level (max 90 dB at 1meter). Capacity ratings and power consumption with operating points clearly indicated, shall be submitted.  Capacity   shall   be ascertained by measurements of chilled water flow rate and temperature   of chilled water in and out of the chilling unit. Power consumption shall be computed from measurements of incoming voltage & input current to the chilling machine.

2.1.13	WITNESS TEST

Unit shall be witness tested at manufacturer work with the VFD (being supplied to project).

Prior to shipment, the chiller shall be witness tested at manufacturer's work at 100%,75%,50%,25 as per AHRI 550-590 std on AHRI certified test bed. Chilling machines shall be subjected to inspection and witness of performance tests in presence of Owner/PMC-in-charge to verify various performance parameters as confirmed by contractor. All the charges/expenses for the Employer’s representative shall be as per conditions in tender document.

One chiller of each type /capacity shall be factory Performance tested in the presence of Owner/PMC or their representative in AHRI-accredited test facility.

| Chiller Testing Required at |  |  |  |  |
| --- | --- | --- | --- | --- |
| Percentage unloading (%) | 100 | 75 | 50 | 25 |
| Condenser Water Temp (In Deg F) | 88 | 76.5 | 65 | 65 |
| FF Correction | Required | Required | Required | Required |

# C.3	AIR COOLED SCREW HEAT PUMP MACHINES WITH VFD STARTER (Eurovent Certified)

1. 	SCOPE

Scope of this sub-section comprises the design, supply, erection, testing and commissioning of air cooled semi hermetic screw heat pump with VFD starter driven compressors confirming to these specifications.

2. 	TECHNICAL SPECIFICATIONS

The heat pump shall have two or more mono or twin type screw compressors in two or more refrigeration circuits.

The water chilling machine shall be complete with full charge of Zero ODP Environmental friendly refrigerant R134a and oil, vibration isolation pads and accessories, factory assembled and tested for rated capacity.

3. 	COMPRESSOR

The unit will be provided with multiple Semi-hermetic screw compressors suitable for 415 +/- 10% volts, 3 phase, 50 Hz. Each compressor should have one inverter managed by the unit microprocessor for infinitely modulating the capacity. An integrated high efficiency oil separator should be there to maximise the oil separation. Starter should be inverter (VFD) type. Refrigerant should be charged at factory & then despatched.

4. 	CONDENSER

The condenser coil shall be air cooled type with high efficiency inner grooved copper tubes. Condensers shall be air cooled type of copper tube and aluminium fin construction. Condenser shall be complete with provisions for refrigerant piping connections and any other standard accessory necessary with the equipment supplied. Micro channel heat exchangers (Al-Al) are not acceptable.

The condenser fans shall be propeller/axial type with low noise, directly driven by a motor and positioned for vertical air discharge. The draw-through design provides uniform airflow over the entire condenser coil shall be, thus ensuring proper condensation throughout the coil. The condenser fan motors shall be designed for outdoor operation in high ambient temperatures and shall be protected with circuit breakers provided in the panel. They shall operate or 415 Volts, 3 Phase, 50 Hz supply.

5. 	EVAPORATOR

Chillers shall be complete with the following accessories:

- Suitable sized Heat Exchanger: it can be Shell and Tube type DX or flooded

type.

- Electronic expansion valves, Necessary drain valves and vent.

c. 	Anti-freeze thermostat.

d. 	Other standard accessories, necessary for the equipment supplied.

e. 	The chiller shall be insulated with factory-installed insulation.

The tubes shall be inner grooved for enhanced heat transfer and rolled into steel tube sheet and sealed.

The evaporators shall be designed on both the refrigerant and water sides for pure counter-flow heat exchange and low refrigerant pressure drops. Both characteristics contribute to the heat exchanger effectiveness and total unit’s outstanding efficiency. The water side shall be designed for 10 bar of maximum operating pressure and shall be with vents and drain.

Each evaporator shall have 2 or more circuits, one for each compressor and is manufactured in accordance to 97/23/EC directive (PED).

6. 	REFRIGERANT PIPING

The unit shall consist of multiple independent refrigerant circuits. Necessary accessories shall be incorporated in the circuit. The cooler and suction lines shall be insulated with polyethylene foam insulation.

Each unit has two or more independent refrigerant circuits and each one includes:

Compressor with integrated oil separator

• Air Cooled Condenser

• Electronic expansion valve

• Evaporator

• Discharge line shut off valve

• Liquid line shut off valve

• Suction line shut off valve

• Sight glass with moisture indicator

• Filter drier

• Charging valves

• High pressure switch

• High and low pressure transducers

7. 	CONTROL CENTRE

The control centre shall high and low pressure cut out & mini circuit breaker for each compressor. The fan motors shall also be protected by overload protectors and mini circuit breakers. The panel shall also contain cycling thermostats for chilled water temperature control, antifreeze thermostats, interconnecting control wiring pressure gages and indicator lights.

Control Section has the following feature.

• Management of the compressor capacity, Inverter, slide and fans modulation.

• Chillers enabled to work in partial failure condition.

• Full routine operation at condition of:

- high ambient temperature value,

- high thermal load,

- high evaporator entering water temperature (start-up).

• Display of evaporator entering/leaving water temperature.

• Display of condensing-evaporating temperature and pressure, suction and discharge superheat for each circuit.

• Leaving water cooled temperature regulation. Temperature tolerance = 0,1°C.

• Compressors and evaporator pumps hours counter.

• Display of Status Safety Devices.

• Start up numbers and compressors working hours equalization.

• Optimized management of compressors load.

• Fans management according to condensing pressure.

• Automatic re-start in case of power supply interruption (adjustable).

• Soft Load.

• Start at high evaporator water temperature.

• Return Reset.

• AOT Reset (optional).

• Set point Reset (optional).

Safety device / logic for each refrigerant circuit

The following devices / logics are available.

• High pressure (pressure switch).

• Low pressure (transducer).

• Condensation fan Magneto-thermal.

• High Discharge Temperature on the compressor.

• Phase Monitor.

• Low pressure ratio.

• High oil pressure drop.

• Low oil pressure.

System security

The following securities are available.

• Phase monitor.

• Freeze protection.

8.	 INSTALLATION

The installation shall be carried out in accordance with the best Owner/PMCing practices to the complete satisfaction of Owner/PMC-in-charge to ensure installation free vibration and noise considered objectionable.

9.	TESTING

Standard manufacturer’s test certificates shall be submitted.

10. 	PAINTING

The supplier shall be responsible to restore the equipment to original condition in case of any scratches or damages to the equipment up to the handing over the same to the Employer.

11. 	TECHNICAL DATA

The contractor shall submit complete technical data for selection of various components supported by the relevant literature.

The following items of works shall be provided: -

12.1	The contractor shall be responsible for the dimensional adequacy and accuracy and quality of these works and shall ensure that these are completed as per the required time schedule. HVAC contractor will furnish sufficient information and technical inputs required for these work which will be carried out by other and responsible for the same. VAC contractor will have intermittent check during the work progress as well as after final completion of the said work.

12.2	Provision of main 3 PH, 50 Hz, 415 volts A.C. main electric supply cables up to the A/C. equipment with proper cable dressing with appropriate glands fitting and terminating inside all HVAC equipment panels room and at Various locations of Blowers, Propeller Fans etc. up to the main switches/circuit breakers of the A.C. Panel. Single phase 50 Hz, 220 Volts supply up to each.

12.3	Civil works, such as wall/floor trenching, equipment foundations, AHU Rooms, Chiller Supports, etc. and finishing of grille openings

12.3	False ceiling to cover the ducts and drop ceiling as required.

12.4	Floor traps near all the Air Handling Units and in the Pump room, for drains.

1.5	Carpentry work like provision of wooden frames in wall opening in the partitions, false ceiling, floors etc.  for fixing grilles, diffusers, dampers, piping and ducting entry etc.

15.	Test data

The plant whole system shall be tested in witness of Owner/PMC-in-charge as per specifications given elsewhere and complete test data shall be furnished on prescribed data sheet.

18.	Technical data, “Makes of Equipments” & Data Confirmation sheet

18.1	The contractor shall furnish complete “Technical Data” and “Data sheet” of the equipment offered by him as required under the heading “Technical Data”, “Makes of Equipments” and “Data Confirmation sheet” respectively.

18.2	The contractor shall also provide data on other installation in North India where similar chillers have been installed giving names of installation, capacity etc.

- Equipment Selection

19.1	The selection of various equipment along with equipment data shall be sent for 	approval prior to ordering.

19.2	It is imperative that the selection of pumps sent for approval should include pump curves also.

20.	Life Cycle Cost

The contractor shall provide life cycle cost of the plant for 20 years.

21	Performance guarantee

21.1	The contractor  shall  guarantee  that  the  air conditioning  plant shall maintain the design inside temperature within   1 oC  tolerance and the relative humidity  shall  not  exceed  the specified  limit.

21.2   	The   contractor shall   guarantee   that the   capacity of various components as well as the whole system shall not be less than specified.

22.	Foreign exchange

    - The contractor shall make his own arrangements to procure the necessary, specified equipment for which no foreign exchange shall be made available by the Employer.

# C.4	PUMPING SYSTEM

# C.4.1 PUMPS

1.1	SCOPE

The scope of this section comprises the design, supply, erection, testing and commissioning of water pumps conforming to these Specifications and approval from Owner/PMC-in-charge.

1.2	TYPE

The type and size of all chilled water, condensing water, cold water and condensate drain pumps for air conditioning applications shall be in accordance with requirement of approved Drawings and Technical Specification.

1.3	CAPACITY

Water flow rates and head of the pumps shall be in accordance with the requirements of Technical Specification.  Pump casing shall be cast iron suitable for 275 psig and 400 psig working pressure and design pressure respectively at 140 deg F in case of condensing water pumps.  Rest of the pumps, pump casing shall be cast iron, suitable for 175psig working pressure at 140°F. The casing shall be hydrostatically tested to 150% maximum working pressure.

1.4	SPLIT CASING / Back pullout PUMPS

a.	Pump casing shall be close-grained cast iron of heavy section, horizontally/vertically split, making possible complete servicing of rotating parts without breaking piping or motor connections. Motor to pump connection shall be of the flexible coupling type. Suction passages shall be volute in form, promoting smooth entry to impeller and increased efficiency.  Impeller shall be bronze or gun metal, double suction, enclosed type, hydraulically balanced and passages smooth-finished   for   minimum friction and maximum efficiency.  Impeller rings shall be secured from relative movement by tongue and groove fittings. Shaft shall be steel, protected by gunmetal sleeves extending through stuffing boxes. Stuffing boxes shall be extra deep, water sealed with renewable bushes. Shaft shall be supported in ball /journal bearings, grease   lubricated, contained   in   easily removable housing.  Pumps shall be fitted with mechanical seals, an air valve, two grease lubricators, drain plug and water seal drain connections.

b.	Motor shall be energy efficient (EFF-1), totally enclosed, fan-cooled, Class-F insulation. Motor shall be specially designed for quiet operation and its speed shall not exceed 1440 rpm. The motor rating shall be such as to ensure non overloading of the motor throughout its capacity range.  Motor shall be suitable for 415±10% volts, 3 phase, 50 cycles AC, power supply.

c.	Base shall be of a size suitable for the pump, motor and shaft and shall be constructed of cast iron or welded steel.  Flexible coupling shall be protected by a guard mounted on the common base.

d.	Installation: The pump shall be installed on a concrete foundation with vibration isolators as per Approved-for-Construction shop drawings/Technical Specification.

e.	Back pull out end suction pumps shall be used upto 20 HP or 1800 Usgpm (Whichever is lower). Double suction vertical split casing pumps shall be used for water flow of 1800 Usgpm and above.

1.5	MONOBLOC PUMPS

a.  	Pump   shall be monobloc end-suction design directly connected to motor. The pump casing shall be of cast iron. Impeller shall be cast iron, hydraulically balanced and keyed to shaft. Stuffing boxes shall be integral with casing and water sealed. Shaft sleeve shall be of gun metal extending through stuffing boxes.

b.  	Motor   shall be drip and splash proof, designed as integral part of pump.  Motor shall be suitable for 415±10% volts, 3 phase, 50 cycles AC power supply.

c.  	Installation:  The pump base shall be mounted on a concrete foundation as per on Approved-for-Construction shop drawings.

1.6	CLOSE / LONG COUPLED VERTICAL IN-LINE Pumps

Pump shall be single stage, single suction Vertical In-Line type, with rising head to shut off pump characteristics along with pump flows and heads and motor speed, efficiency, enclosure and power requirements etc.

Pump casing shall be cast iron, suitable for the working pressure as specified in clause 3.3 at 140°F. The casing shall be hydrostatically tested to 150% maximum working pressure. The casing shall be radially split to allow removal of the rotating element without disturbing the pipe connections. The casing shall be provided with NPT threaded companion flanges, for the appropriate pump size, with gaskets and hardware.

Pump impeller shall be fully enclosed type. The impeller shall be keyed and secured to the pump shaft by stainless steel fittings.

The pump shaft shall be a stainless steel stub shaft for frame 56 motors. The steel motor shaft shall be enclosed by a bronze shaft sleeve, on other motor frame sizes.

Mechanical Seal shall be single spring inside type in close couple pump and outer side of pump casing in case of long coupled pump (for easy replacement) with Carbon and Ni-Resist faces, EPDM elastomer, stainless steel spring and hardware. (Carbon and Ceramic faces, with Buna elastomer and brass hardware, on frame 56 motor units). Provide factory installed seal vent line, piped from the seal area to the pump suction connection.

1.7	LUBRICATION

Upon installation of the complete system and before testing, the pump shall be lubricated in strict accordance with the manufacturer’s instructions.

1.8	PUMP ALIGNMENT

Split casing pumps, prior to testing, shall be aligned with a dial indicator within 0.05 mm.

1.9	PAINTING

All pumps, motors and bases shall be supplied with approved finish.  Shop coat of paint that have become marred during shipment or erection shall be cleaned off with mineral spirits, wire brushed and spot primed over the affected areas, then coated with enamel paint to match the adjoining areas.

1.10	PERFORMANCE DATA

Pump performance curves and power consumption with operating points clearly indicated shall be submitted and verified at the time of testing and commissioning of the installation.

1.11	TESTING

Pump performance shall be computed from the pump curves provided by manufacturer. All pumps shall be tested at factory as per relevant BIS codes.

# C.4.2. VARIABLE SPEED PUMPING SYSTEM

2.1	SCOPE

The scope of this section comprise the design, supply, erection, testing and commissioning of variable speed pumping package consisting of following:

a.	Individual Components

b.	Pump Control Panel

c.	Adjustable Frequency Drive

d.	Different pressure transmitted (Min. 1 Nos. per zone)

e.	Logic Programming for sequence of Operation

f.	Power wiring and control wiring shall be carried out by installation contractor as shown on the field connection drawings and wiring diagrams supplied with the pumping package.

2.2	REFERENCES

a.	ANSI 	-	American National Standards Institute

b.	NEMA	-	National Electrical Manufacturers Association

c.	UL	-	Underwriters Laboratories Inc.

d.	ETL	-	Electrical Testing Laboratories

e.	CSA	-	Canadian Standards Association

f.	NEC	-	National Electrical Code

g.	ISO	-	International Standards Organization

h.	IEC	-	International Electrochemical Commission

2.3	SUBMITTALS

Submittals shall include the following and shall be specific to this project. General Submittals shall not be accepted.

a.	System summary sheet.

b.	Sequence of operation

c.	Shop drawing indicating dimensions, required clearances and location and size of each field connection.

d.	Power and control wiring diagrams.

e.	System profile analysis including variable speed pump curves and system curve. The analysis shall also include pump, motor and Adjustable Frequency Drive (AFD) efficiencies, job specific load profile, staging points, horse power and kilowatt/hour consumption.

f.	Pump data sheets.

2.4	QUALITY ASSURANCE

a.	The pumping package shall be assembled by the pump manufacturer. An assembler of pumping systems not actively engaged in the design and construction of centrifugal pumps shall not be considered a pump manufacturer. The manufacturer shall assume “Unit Responsibility” for the complete pumping package. Unit responsibility shall be defined as responsibility for interface and successful operation of all system components supplied by the pumping system manufacturer.

b.	The manufacturer shall have a minimum of 10 (ten) years of experience in the design and construction of variable speed pumping systems.

c.	The local supplier of Chilled Water Variable Speed Pumping System (VSPS) shall have relevant expertise in all aspects of design, application Owner/PMCing, installation, programming, interfacing, commissioning and after sales service.  Supplier must have commissioned minimum 25 sets of chilled water VSPS in India.

d.	All functions of the variable speed pump control system shall be tested at the factory prior to shipment. This test shall be conducted with motors connected to AFD output and it shall test all inputs, outputs and program execution specific to this application.

e.	The manufacturer shall be fully certified by the International Standards Organization per ISO 9001. Proof of this certification shall be furnished at time of submittal.

f.	Manufacturer shall be listed by Underwriter’s Laboratories as manufacturer of packaged pumping systems.

g.	Tenderer shall comply with all sections of this specification relating to packaged pumping systems.

2.5	MANUFACTURED UNITS

a.	Furnish and install a Variable Speed Pumping System as per approved manufacturers.

b.	The control system shall include as, a minimum, the programmable logic pump controller, adjustable frequency drive(s) and remote sensor / transmitters as indicated in the approved drawings and Technical Specification. Additional items shall be included as specified or as required to properly execute the sequence of operation.

c.	The variable speed pump logic controller, adjustable frequency drives, AFD bypass as indicated in Technical Specification, and remote sensor / transmitters shall be shipped as individual components to the job site.

d.	Pump logic controller, adjustable frequency drives, sensor / transmitters and related equipment shall be installed by the contractor as shown on the approved drawings.

e.	Power wiring shall be installed by the contractor as shown on the field connection approved drawings and wiring diagrams supplied with the pumping package.

f.	Low voltage wiring shall be installed by the contractor as shown on the field connection approved drawings and wiring diagrams supplied with the pumping package.

2.6	PUMP LOGIC CONTROLLER

a.	The pump logic controller assembly shall be listed by and bear the label of Underwriter’s Laboratory INC. (UL). The controller shall meet Part 15 of FCC regulations pertaining to class A computing devices. The controller shall specifically have designed for variable speed pumping applications.

b.	The controller shall function to a proven program that safeguards against hydraulic conditions including: -

I.	Pump flow surges

ii.	Hunting

iii.	End of curve

iv.	System over pressure.

v.	NPSHR above NPSHA

vi.	Motor overload

c.	The pump logic controller shall be capable of receiving up to two discrete analog inputs from zone sensor / transmitter as indicated on the plans.  It will then select the analogue signal that has deviated the greatest amount from its setpoint.  This selected signal shall be used as the command feedback input for a hydraulic stabilization function to minimize hunting.  Each input signal shall be capable of maintaining a different set point value.  Controller shall be capable of controlling upto three pumps in parallel.

d.	The pump logic controller shall have an additional analog input for a flow sensor. This input shall serve as the criteria for the end of curve protection algorithm.

e.	The hydraulic stabilization program shall utilize a proportional-integral-derivative control function. The proportional, integral and derivative values shall be user adjustable over an infinite range.

f.	The pump logic controller shall be self-prompting. All messages shall be displayed in plain English. The operator interface shall have the following features:

i. 	Multi-fault memory and recall last 10 faults and related operational data

ii.	Red fault light, Yellow warning light and Green power on light.

iii.	Soft-touch membrane keypad switches.

g.	The display shall have four lines, with 20 characters on three lines and eight large characters on one line.  Actual pump information shall be displayed indicating pump status.

h.	Controller shall be capable performing the following pressure booster function:

i.	Low suction pressure cut-out to protect the pumps against operating with insufficient suction pressure.

ii.	High system pressure cut-out to protect the piping system against high pressure conditions.

iii.	No flow shut down to turn the pumps off automatically when system demand is low enough to be supplied by hydro pneumatic tank. No flow shutdown shall require any external flow meters, flow switches, nor pressure switches to determine when a No Flow condition exists.

j.	The following communication features shall be provided to BAS:

i.	Remote system start / stop non-powered digital input.

ii.	Failure of any system component.  Output closes to indicate alarm condition.

iii.	One 4-20 mA output with selectable output of:

- Frequency

- Process Variable

- Output Current

- Output power.

k.	The following communication features shall be provided to the building automation system via an RS-485 port utilizing Johnson Controls Metasys N2 protocol or equivalent protocol.

i.	Individual Analog Input

ii.	Individual Zone Set Points.

iii.	Individual Pump / AFD on/off status.

iv.	System percent speed.

v.	System Start / Stop command

vi.	System operation mode.

vii.	Individual KW signals.

viii.	System flow, when optional flow sensor is provided.

l.	The pump logic controller shall be in a NEMA 1 Enclosure.

2.7	ADJUSTABLE FREQUENCY DRIVE

a.	The adjustable frequency drives shall be Pulse Width Modulation (PWM) type, microprocessor controlled design.

b.	The Adjustable Frequency Drive (AFD), including all factory installed option, be tested to UL standard 508.  The AFD shall also meet C-UL and be CE marked and built to ISO 9001 standards.

c.	The AFD shall be housed in a IP 55 enclosure.  AFF with plastic enclosure shall not be acceptable.

d.	The AFD shall employ and advanced sine wave approximation and voltage vector control to allow operation at rated motor shaft output speed with no derating.  This voltage vector control shall minimize harmonics to the motor to increase motor efficiency and lift.  Power factor shall be near unity regardless of speed or load.

e.	The AFD shall have balanced DC link reactors to minimize power line harmonics AFDs without a DC link reactor shall provide a 3% impedance line reactor.

f.	Input and output power circuit switching can be done without interlocks or damage to the AFD.

g.	The following customer modifiable adjustments shall be provided:

i.	Accel time.

ii.	Decel time.

iii.	Minimum Frequency.

iv.	Maximum Frequency.

h.	RS-485 communication for Johnson Controls N2 shall be available and provided as an option.

i.	An automatic energy optimization selection feature shall be provided.  This feature shall reduce voltage when lightly loaded and provide a 3% to 10% additional energy savings.

j.	The AFD shall be suitable for upto 3300 feet elevation above sea level without derating.  Maximum operating ambient temperature shall not less than 104 degrees F.  AFD shall be suitable for operation in environments upto to 955 non-condensing humidity.

k.	The AFD shall be capable of displaying the following information in plain English via an alphanumeric display:

i.	Frequency.

ii.	Voltage

iii.	Current

iv.	Kilowatts per hour

v.	Fault Identification.

vi.	Percent Torque.

vii.	Percent Power

viii.	RPM

2.8	AUTOMATIC AFD BYPASS

a.	Variable speed pumping system shall be equipped with an automatic bypass.

b.	Bypass shall consist of a main power disconnect with ground fault protection, a pair of interlocked contractors and a motor overload relay. All are to be mounted in a NEMA 1 enclosure.

2.9	SENSOR / TRANSMITTERS

a.	Provide field mounted differential pressure sensor transmitters.  Unit shall transmit an isolated 4-20mA dc signal indicative of process variable to the pump logic controller via standard two wire 24 DC system. Unit shall have a corrosion resistant steel body with 1/8” NPT process connection. It shall have a NEMA 1 electrical enclosure capable of withstanding 450 PSI static pressure.  Accuracy shall be within 0.5% of full span.  The installation contractor shall ensure that these differential pressure sensors are enclosed within pilfer proof housing such MS plate housing with lockable access panel.

# C.4.3 SECONDARY PUMPS

a.	SCOPE

The scope of this section comprise the design, supply, erection, testing and commissioning of water pumps conforming to these specifications and in accordance with requirements and as per approval from Owner/PMC-in-charge.

b.	TYPE

The type and size of secondary chilled/hot water, and pumps for air conditioning applications shall be in accordance with requirement of approved Drawings and Technical Specification and as per approval from Owner/PMC-in-charge.

c.	CAPACITY

Water flow rates and head of the pumps shall be in accordance with the requirements as per actual calculations and approval from Owner/PMC-in-charge.

d.	SPLIT CASING PUMPS

i.	Pump casing shall be close-grained cast iron of heavy section, horizontally/vertically split, making possible complete servicing of rotating parts without breaking piping or motor connections. Motor to pump connection shall be of the flexible coupling type. Suction passages shall be volute in form, promoting smooth entry to impeller and increased efficiency.  Impeller shall be bronze or gun metal, double suction, enclosed type, hydraulically balanced and passages smooth-finished for minimum friction and maximum efficiency.  Impeller rings shall be secured from relative movement by tongue and groove fittings. Shaft shall be steel, protected by gunmetal sleeves extending through stuffing boxes. Stuffing boxes shall be extra deep, water sealed with renewable bushes. Shaft shall be supported in ball /journal bearings, grease lubricated, contained in easily removable housing. Pumps shall be fitted with mechanical seals, an air valve, two grease lubricators, drain plug and water seal connections.

ii.	Motor shall be energy efficient, totally enclosed, fan-cooled, Class-F insulation and suitable for operation on Variable Frequency Drive (VFD). Motor shall be specially designed for quiet operation and its speed shall not exceed 1440 rpm. The motor rating shall be such as to ensure non overloading of the motor throughout its capacity range.  Motor shall be suitable for 415 ± 10% volts, 3 phase, 50 cycles AC, power supply.

iii.	Base shall be of a size suitable for the pump, motor and shaft and shall be constructed of cast iron or welded steel.  Flexible coupling shall be protected by a guard mounted on the common base.

iv.	Installation: The pump shall be installed on a concrete foundation as shown in Approved-for-Construction shop drawings.

v.	Each pumps shall be provided with certified performance curves showing power absorbed and corresponding flow rates by varying the speed. Tests shall be done at factory and may be witnessed by Owner/PMC-in-charge.

e.	PUMP ALIGNMENT

Split casing pumps, prior to testing shall be aligned with a dial indicator within      0.05 mm.  Monobloc pumps shall be factory aligned with motor on common base, and need not be realigned at site.

f.	PERFORMANCE DATA

Pump performance curves and power consumption with operating points clearly indicated shall be submitted and verified at the time of testing and commissioning of the installation.

g.	TESTING

Pump performance at site shall be computed from the pump curves provided by manufacturer.

4	PAINTING

All variable pumping system, pumps, motors and bases shall be supplied with approved finish.  Shop coat of paint that have become marred during shipment or erection shall be cleaned off with mineral spirits, wire brushed and spot primed over the affected areas, then coated with enamel paint to match the adjoining areas.

4.1	SEQUENCE OF OPERATION

a.	The system shall consist of a pump logic controller, multiple pump / VFD sets, with manual and automatic alternation and pump staging.

b.	The pumping system shall start upon the closure of customer’s contact when the pump logic controller Mode of Operation selector switch is in the REMOTE position.

c.	When the pump logic controller selector switch is in the LOCAL position, and start command is given via operator interface, the pumping system shall operate automatically.

d.	Sensor / transmitters shall be provided as indicated on the plans.

e.	Each sensor / transmitter shall send a 4-20 mA signal to the pump logic controller, indicative of process variable condition.

f.	The pump logic controller shall compare each signal to the independent, Owner/PMC / user determined set points.

g.	When all set points are satisfied by the process variable, the pump speed shall remain Constant at the optimum energy consumption level.

h.	The pump logic controller shall continuously scan and compare each process variable to its individual set point and control to the least satisfied zone.

i.	If the set point cannot be satisfied by the designated lead pump, the pump logic controller shall initiate a timed sequence of operation to stage a lag pump.

j.	The lag pump shall accelerate resulting in the lead pump(s) decelerating until they equalize in speed.

k.	Further change in process variable shall cause the pumps to change speed together.

l.	When the set point criteria can be safely satisfied with fewer pumps, the Technologic pump logic controller shall initiate a timed destage sequence and continue variable speed operation.

m.	As the worst case zone deviates from set point, the pump logic controller shall send the appropriate analog signal to the VFD to speed up or slow down the pump / motor.

n.	In the event of a VFD fault, the pump logic controller automatically initiates a times sequence of events to start the redundant pump / VFD set in the variable speed mode.  The redundant variable speed system shall be started through the pump logic controller.

o.	Upon VFD fault(s), the pump controller shall display an alarm condition through a plain English message.

p.	VFD fault indication shall be continuously displayed on the operator interface of the pump until the fault has been corrected and the controller has been manually reset.

q.	In the event of the failure of a zone sensor / transmitter, its process variable signal shall be removed from the scan / compare program.  Alternative zone sensor / transmitters, if available, shall remain in the scan / compare program for control.

r.	Upon sensor failure a plain English warning message shall be displayed on the operator interface of the pump logic controller.

s.	In the event of failure to receive all zone process variable signals, a user selectable number of VFDs shall maintain a user adjustable speed, reset shall be automatic upon correction of the zone failure.

# C.5	COOLING TOWERS

1	SCOPE

The scope of this section comprises the design, supply, erection, testing and commissioning of cooling towers in accordance with requirements of schematic Drawings, actual calculations and technical specifications and as per approval from Owner/PMC-in-charge.

2	TYPE

Cooling Towers shall be induced draft /forced draft in accordance with requirement of Drawings and of the Technical Specification. Cooling towers shall be as per CTI or shall be tested at site as per CTI norms (for green buildings only). In case of multiple fans in cooling tower, HVAC contractor to provide an electrical panel for one incoming and multiple outgoings/ (including starters DOL/ Star delta / VFD as required) equal to number cooling tower fans. This panel shall be included in cooling tower rate.

3	INDUCED DRAFT COOLING TOWER

Cooling Towers shall be suitable for outdoor use. Tower shall be vertical, induced draft, counter/cross flow type.  FRP construction, in rectangular/ square /octagonal profile, complete with fan, motor, diffusion deck spray section, eliminators, steel supports, and sound attenuation equipment where called for in Technical Specification.

a.	Capacity

The cooling tower capacities shall be as per the approved Drawings and Technical Specification.

b.	Side Casing

This shall be made out of FRP construction of minimum 5 mm thick and UV stabilized with smooth surface on both sides for minimum resistance to air flow. It shall have sufficient   structural   strength   to adequately withstand high wind velocities and vibration. The casing may be installed in the reinforced cement concrete basin if so identified in drawings, or in Technical Specification.  The tower supporting structure shall be made out of hot dipped galvanized tubular frame.  Air intake shall be all along the sides so that tower can be installed quite independent of prevailing wind direction. Anodized aluminium or PVC louvers integrated with fill UV stabilized PVC fill and backed up by galvanized bird screen / FRP Louvers shall be provided at air intake.  Sufficient clearance between casing and adjoining structures shall be provided to enable servicing and periodic cleaning.

c.	Cold Water Basin

Cold water basin shall be a min. 600 mm deep slump and made out of 5 mm thick FRP construction and UV stabilized on which cooling tower super structure shall be supported.  RCC suction tank with easily removable double brass strainers may be provided with this basin, if separately identified in approved drawings or in Technical Specification.

Basin fittings shall include the following:

i.	Bottom outlet.

ii.	Screened suction assembly.

iii.	Drain connected to the side / underside of basin.

iv.	Overflow connected to the side of basin.

v.    	Built-in   bleed off attached to inlet   header discharging through polyethylene tube into overflow pipe.

vi.	Ball type automatic make up water valve.

vii.	Quick fill connected to the side of basin.

viii.	Equalizing connection and balancing valve for multiple CTs.

d.	Distribution System

Hot water distribution system shall   comprise of header and branch arms system or open pan gravity flow system.

e.	Filling

Fillings shall be made of corrosion proof and rigid PVC film in honey comb design and arranged in square / rectangular form. Fill sheets shall be suspended from H.D.G steel structural tubing supported from the lower structure & shall be elevated above the floor of the cold water basin to facilitate cleaning and easy replacement.  They shall be arranged in such a manner to ensure negligible resistance to air flow and to eliminate back water spots and prevent fouling through scales that may form.  In order to reduce carry-over losses through entrainment   of moisture drops in air stream, PVC drift eliminator shall be installed.

f.	Mechanical Equipment

The tower shall be provided with low speed fan running at less than 360 RPM through gear reducer. Direct driven fan speed shall not exceed 700 RPM. Fan shall be of the propeller type light-weight rotor fitted with multiple aerofoil blades.  The entire fan assembly shall be statically and dynamically balanced.  Fan shall be driven by 415±10% volts, 3 phase, 50 cycles, AC supply, energy efficient motor totally-enclosed, fan-cooled, weather-proof construction, designed and selected to operate in humid air stream. Fan shall be protected by a fan guard and bird screen of galvanized steel construction to prevent birds from nesting during idling period & shall be easily accessible for inspection and maintenance.  A service   ladder (Aluminium construction) shall also be provided for greater convenience.  The mechanical equipment assembly shall be adequately supported on a rugged steel base welded to tubular support assuring vibration-free support.  Fan guard and bird screen (of galvanized steel construction) shall be provided to prevent birds from nesting during idling periods. Gear-reducer shall be of spiral bevel type. G.S.S canopy shall be provided over the fan motor for protection against rain water. Care shall be taken that fan air is not restricted. Motor terminal box shall be made water tight.

4     	FORCED   DRAFT COOLING TOWER

Forced draft cooling tower shall be FRP   construction of minimum 5 mm thick and UV stabilized and structural framed, cross-flow forced draft type, suitable for outdoor use.  Tower shall be complete with fan, motor, diffusion deck, spray section and eliminator plate. Tower shall be selected for low height and lowest possible noise level as defined in Technical Specification.

a.	Capacity

The cooling tower capacity shall be as per actual calculations and Technical Specification and as per approval from Owner/PMC-in-charge.

b.	Casing

Casing and basin shall be of FRP of minimum 3 mm / 5 mm thick respectively and sealed for water tightness. All joints and corners shall be sealed and an aluminium ladder shall be provided to reach upto the top of cooling tower.

c.	Cold Water Basin

Cold water basin shall be a with deep slump in which cooling tower superstructure shall be supported.  Easily removable brass-strainers shall be provided with the basin and pump suction shall be provided after strainers.

Basin fittings shall include the following:

i.	Side outlet.

ii.	Screened suction assembly with openable cover of steel sheet.

iii.	Drain connected to the side / underside of basin.

iv.	Overflow connected to the side of basin.

v.    	Built-in   bleed off attached to inlet   header discharging through polyethylene tube into overflow pipe.

vi.	Ball type automatic make up water valve.

vii.	Quickfill connected to the side of basin.

viii.	Equalizing connection/balancing valve for multiple cooling towers.

ix.	Bird screen at air inlet/outlet of the fan.

d.	Distribution System

Hot water distribution system shall be comprising of header and branch arm system or open pan gravity flow system suitable for high pressure.

e.	Filling

Fillings shall be made of corrosion proof and rigid UV stabilized PVC film in honey comb / modular design and arranged in square / rectangular form. Fill sheets shall be suspended from H.D.G steel structural tubing supported from the lower structure & shall be elevated above the floor of the cold water basin to facilitate cleaning and easy replacement.  They shall be arranged in such a manner to ensure negligible resistance to air flow and to eliminate back water spots and prevent fouling through scales that may form.  In order to reduce carry-over losses through entrainment   of moisture drops in air stream, PVC drift eliminator shall be installed.

f.	Mechanical Equipment

Fan shall be centrifugal/axial fan, aluminium alloy aerofoil construction. The entire fan assembly shall be statically and dynamically balanced. Fan motor shall be low RPM, suitable for 415±10% volts, 3 phase, 50 cycles AC supply, energy efficient electric   motor, totally enclosed, fan-cooled, weather-proof construction. The noise level from cooling tower shall be less than 65 dB from 3-meter distance all around the cooling tower. (45 dBA at 3m distance for low noise cooling towers) The mechanical equipment assembly shall be adequately supported through galvanized steel angle frame work. The hot and humid air shall be discharged at the top level. Galvanized steel construction bird screen at outlet shall be provided to prevent birds from nesting during idling period.

5	PERFORMANCE DATA

Complete performance ratings and power consumption at varying loads and outdoor wet bulb temperatures, shall be submitted and verified at the time of testing and commissioning of the installation.

6	TESTING

Capacity of the cooling tower shall be computed from the measurements   of   water   flow, incoming/outgoing   water temperatures and ambient air wet bulb temperature using accurately calibrated mercury-in-glass thermometers. Computed ratings shall conform to the specified capacities and quoted ratings.  Power consumption for cooling towers shall be computed from measurements of incoming voltage and input current.

# C.6	AIR HANDLING UNITS with Air Purification System

1	SCOPE

The scope of this section, comprises the design, supply, erection, testing and commissioning of double skin construction   air handling units, conforming to these Specifications and in accordance with requirements of schematic drawings and of the Technical Specification and as per approval from Owner/PMC-in-charge.

2	TYPE

The air handling units shall be double skin construction, draw-thru type comprising of various sections, filter section, coil section and fan section, mixing box, (wherever the return air and fresh air are ducted) as shown on approved drawings and included in Technical Specification.

3	CAPACITY

The air handling capacities, maximum motor horse power and static pressure shall be as shown on schematic Drawings, actual calculation and as per approval from Owner/PMC-in-charge.

4	CASING

Double skinned PUF panels shall be   23 / 46 mm thick made   of galvanized steel, pressure injected with foam insulation (density 40 kg/m3) with K factor not exceeding 0.02 Watt/Mc shall be fixed to 1.5 mm thick aluminium alloy twin box section structural framework with stainless steel screws.  Outer   sheet   of panels shall be made   of   galvanised preplasticised sheet of    0.63 mm thick, and inner sheet of 24 Gauge plain G.I. Sheet.

The entire framework shall be mounted on an aluminium alloy or galvanized steel (depending on size) channel base as per manufacturer’s recommendation. The panels shall be sealed to the framework by heavy duty gaskets held captive in the framed extrusion.  All panels shall be detachable or hinged.  Hinges shall be made of die cast aluminium / hard nylon with stainless steel pivots, handles shall be made of hard nylon and   be operational from both inside and outside of the unit.  Units supplied with various sections shall be suitable for onsite assembly with continuous foam gasket. All fixing and gaskets shall be concealed.

Units shall have hinged, quick opening access door in the fan section and also in filter section where filters are not accessible from outside. Access doors shall be double skin type.

Condensate drain pan shall be fabricated from 18 gage stainless steel sheet with all corners welded. It shall be isolated from bottom floor panel with 19 mm elastomeric nitrile rubber.

5	MIXING BOX

AHU’s requiring mixing boxes as specified in Technical Specification shall be complete with fresh and return air dampers.

6	THERMAL BREAK PROFILE

AHU’s such as TFA units, AHU with mixing box having return air ducted shall be provided with thermal break profile as indicated in Technical Specification. Also these AHU’s shall be provided with 46 mm thick panel.

7	DAMPER

Dampers shall be opposed blade type. Blades shall be made of double skinned aerofoil aluminium sections with integral gasket and assembled within a rigid extruded aluminium alloy frame. All linkages and supporting spindles shall be made   of aluminium or nylon, turning in Teflon bushes.   Manual dampers shall be provided with a bakelite knob for locking the damper blades in position.  Linkages shall be extended wherever specified   for motorised operation. Damper frames shall be sectionalised to minimise blade warping. Air leakage through dampers when in the closed position shall not exceed 1.5% of the maximum design air volume flow rate at the maximum design air total pressure.

8	MOTOR AND DRIVE

​Fan motors shall be energy efficient and shall be 415±10% volts, 50 cycles, three phases, totally enclosed fan-cooled class F, with IP-55 protection. Motors shall be especially designed for quiet operation. Motor shall be suitable to operate with direct driven plug fans and frequency converter. Frequency converter (VFD) shall be supplied by the AHU manufacturer for all AHUs with direct driven plug fans for the complete control of motor rpm.

9	FAN

9.1 Plug Fan for AHU

​Fans shall be AMCA Certified backward curved plug fan for Sound and Air Performance in accordance with AMCA 210 & AMCA 300 with High efficient design blades for given duty condition. The entire Fan with Motor assembly will be balanced at supplier’s works before dispatch. Fans driven by variable frequency drive. Fans shall be selected for high efficiency and low noise. Fan array with multiple fans can be used wherever required. Plug fan shall be VFD compatible. Fan motor assembly shall be statically and dynamically balanced as per relevant ISO/AMCA/EUROVENT standard. AMCA Fan Curve shall be submitted with AHU Technical detail.

​Motors shall be mounted inside the AHU casing and be totally enclosed, fan cooled with class ‘F’ insulation.

​Both fan and motor assemblies shall be mounted on powder coated MS/galvanized steel (depending on size) base frame.

​Heavy duty anti-vibration mounts shall be provided for isolating the unit casing.  Flame retardant, waterproof silicone rubber impregnated flexible connection shall be provided at the fan discharge.

9.2 PERFORMANCE DATA OF FAN

Plug Fan unit shall be selected for the lowest operating noise level. Fan performance rating and power consumption data with operating points clearly indicated shall be submitted and verified at the time of testing and commissioning of the installation. All Fans Performance curve shall be submitted on AMCA certified for Air and Sound Performance.

10	COOLING COILS

Chilled   water coils shall have 12.5 to 15 mm. dial (O.D) tubes minimum 0.4 mm thick with sine wave aluminium fins firmly bonded to copper tubes assembled in zinc coated steel frame.  Face and surface areas shall be such as to ensure rated capacity from each unit and such that the air velocity across the coil shall not exceed 150 meters per minute.  The coil shall be pitched in the unit casing for proper drainage. The coil shall have copper header with chilled water supply & return connections protruding out of AHU casing by minimum 150 mm and fitted with dielectric coupling for connection with MS pipes.  Each coil shall be factory-tested at 21 kg per sq. m air pressure   under   water. Tube shall   be   hydraulically   / mechanically expanded for minimum thermal contact resistance with fins. Fin spacing shall be 4 - 5 fins per cm.   Water pressure drop in coil shall not exceed 10 PSIG.

All AHU’s shall be provided with minimum 6 Row Cooling Coil.  All TFA AHU’s shall be provided with minimum 8 row cooling coil.  Reheat coil shall be provided to fulfil heating requirements.

In case AHU has multiple coil stacked one above another, intermediate train of SS 304 (18 gauge) shall be provided so that upper level of coil drains into this train. Copper / SS 304 piping shall be provided from this train upto main bottom tray.

Computerized cooling coil selection output shall be submitted. Coil rating shall be as per ARI-410/2006.

11	AIR WASHER SECTION

Air washer section shall be provided in the AHU if required as per design. Air washer section shall be designed for adiabatic humidification. Media shall be wet pad type to allow even distribution of water over entire fill surface area of the pad. Pad shall be selected for minimum adiabatic saturation efficiency of 95%.

Water distribution system shall be with IS-1239 Class C galvanized piping. Mono block pump shall be provided for circulation of water within the unit. Pump shall be mounted inside the unit. Power for the same shall be taken from AHU starter panel. Power / control cabling shall be included. Pump shall be along with necessary Y-strainer, NRV and isolation valves.

Water sump shall be of sufficient height for water storage and providing enough pump NPSH. Sump shall be constructed out of 3mm thick SS-304. Make up water connection along with float valve shall be provided. Drain connection shall be provided at lowest part of sump.

12	FILTERS /Central Air-Purification System

Each unit shall be provided with hybrid air purification system that improves the 	indoor air quality through reducing harmful pollutants like particulate matter (PMx), PM 	2.5, allergens, pollen, smoke, bacteria and pathogens, based on trap & kill technology. 	It shall be a monobloc structured unit specifically designed for integration in Return Air 	paths to AHUs, to centrally capture and kill germs.

13	ACCESSORIES

Each air handling unit shall be provided with manual air vent at high point in the cooling coil and drain plug in the bottom of the coil. In addition, the following accessories may be required at air handling units, their detailed specifications are given in individual sections, & quantities separately identified in Technical Specification.

a.   	Insulated   butterfly   valves, balancing   valves, `Y’ strainer, union & condensate drain piping with ‘U’ trap upto sump or floor drain in air handling unit room, as described in section “Piping”.

b.  	Thermometers in the thermometer wells & pressure gauge (with cocks) within gauge ports in chilled water supply and return lines as per the section “Instruments”.

c.	Water resistance marine light with power cabling.

14	ISOLATORS

Vibration isolators shall be provided with all air handling units. Vibration isolators shall be cushy foot mounting type. Minimum vibration isolation efficiency shall be 90%.

15	FRESH AIR INTAKES

Extruded   aluminium construction duly  anodized (20  microns and  above)  fresh air louvers with birdscreen  and dampers shall be provided in the clear  openings in  masonry  walls  of the air handling  unit  rooms  having atleast  one  external wall.  Louvers, damper, pre-filters, ducts and fresh  air  fan with  speed  regulator  shall  be provided as per approved Drawings and Technical Specifications.  Fresh air dampers shall be of the interlocking, opposed-blade louver  type.  Blades  shall be made  of  extruded  aluminium construction   and  shall  be rattle-free. Dampers  shall  be similar  to those specified in “Air Distribution”. Fresh air fans and fresh air intakes shall be as per the requirements of Technical Specification.

16	PAINTING

Shop coats of paint that have become marred during  shipment or  erection shall be cleaned off with mineral spirits,  wire brushed and spot primed over the affected areas, then  coated with  paint  to  match the finish  over  the  adjoining  shop painted surface.

17	PERFORMANCE DATA

Air handling  unit  shall  be   selected  for  the    lowest operating  noise  level  of the  equipment.  Fan performance rating  and   power consumption data, with  operating  points clearly  indicated  shall be submitted and verified  at  the time of testing and commissioning of the installation.

18	TESTING

Cooling capacity  of  various air handling  unit  models  be computed  from the measurements of air flow and dry  and  wet bulb  temperatures of air entering and leaving the coil. Flow measurements shall be by an anemometer and temperature   measurements   by  accurately calibrated mercury-in-glass thermometers. Computed  results shall  conform    to   the specified  capacities and quoted ratings.  Power  consumption shall  be computed from measurements of incoming voltage  and input current.

# C.7	TREATED FRESH AIR UNIT WITH ENRGY RECOVERY VANTILATOR

1.0 	SCOPE

The scope of this section comprises of the design, supply of double-skin “Treated Fresh Air Units conforming to the following specifications:

2.0	TYPE

The Treated Fresh Air Units shall be two stream units in double skin construction, comprising of supply air section, return air section and Heat Recovery Section. The supply air section shall include the following sections.

Cooling/Heating Section, Microvee filter section, Mixing Box Section, Sound Attenuator Section, Damper Section, Humidifier Section, Inspection Section.

3.0 	CAPACITY

The Treated Fresh Air Units shall be of such capacities as per actual calculations and as per approval from Owner/PMC-in-charge.

4.0 CASING

The units shall be made of extruded Aluminium hollow profile frames. The profile box size shall be of minimum 30 mm for capacities upto 22000 CMH, such that it provides the required mechanical strength and rigidity. The unit should be devoid of any welded construction and should be of cabinet type. All the frames should be assembled using pressure die cast aluminium joints/corners to make a self-supporting frame. The Casing leakage shall be in accordance with relevant EUROVENT standard that is CLASS B.

The panels shall be of double skin construction with both inner and outer steel sheets being minimum 0.8mm thick pre coated & plasticized. 25 mm thick fire retardant, fibre glass insulation shall be sandwiched between the sheets. The fibre glass density shall be 48 kg/m3.

The Inspection and access panels shall be hinged type. The hinges shall be casted, powder coated Zinc alloy. Flushed Locks and Handles shall be of galvanized steel. Other panels will be screwed on to the frame with sealant and soft rubber gasket thus making the joints air tight. All screws used for panel fixing shall be covered with PVC caps.

Special hollow gaskets and seals shall be used on inspection doors and to create separation between the airstreams to ensure negligible air leakage and mixing.

The entire casing shall be mounted on electro galvanized channel frame work with level screws. Condensate drain pan shall be fabricated from18 g GSS/SS construction.

5.0 	SUPPLY AIR SECTION

The supply air section shall comprise of the following:

5.1	FAN SECTION

Plug Fan for AHU

​Fans shall be AMCA Certified backward curved plug fan for Sound and Air Performance in accordance with AMCA 210 & AMCA 300 with High efficient design blades for given duty condition. The entire Fan with Motor assembly will be balanced at supplier’s works before dispatch. Fans driven by variable frequency drive. Fans shall be selected for high efficiency and low noise. Fan array with multiple fans can be used wherever required. Plug fan shall be VFD compatible. Fan motor assembly shall be statically and dynamically balanced as per relevant ISO/AMCA/EUROVENT standard. AMCA Fan Curve shall be submitted with AHU Technical detail.

​Motors shall be mounted inside the AHU casing and be totally enclosed, fan cooled with class ‘F’ insulation.

​Both fan and motor assemblies shall be mounted on powder coated MS/galvanized steel (depending on size) base frame.

​Heavy duty anti-vibration mounts shall be provided for isolating the unit casing.  Flame retardant, waterproof silicone rubber impregnated flexible connection shall be provided at the fan discharge.

PERFORMANCE DATA OF FAN

Plug Fan unit shall be selected for the lowest operating noise level. Fan performance rating and power consumption data with operating points clearly indicated shall be submitted and verified at the time of testing and commissioning of the installation. All Fans Performance curve shall be submitted on AMCA certified for Air and Sound Performance.

5.2    MOTOR AND DRIVE

​Fan motors shall be energy efficient and shall be 415±10% volts, 50 cycles, three phases, totally enclosed fan-cooled class F, with IP-55 protection. Motors shall be especially designed for quiet operation. Motor shall be suitable to operate with direct driven plug fans and frequency converter. Frequency converter (VFD) shall be supplied by the AHU manufacturer for all AHUs with direct driven plug fans for the complete control of motor rpm.

5.3. 	FILTER SECTION

The filter section shall be normally designed for deep folded disposable synthetic prefilters for Class EU3.The filter elements shall be mounted on rails and shall be easily pulled out for replacement. The rails shall be provided with efficient gaskets to minimize the risk of leakage.

6.0	RETURN AIR SECTION

The return air section shall comprise of above sections. The specification for this section shall remain same as defined in 5.1, 5.2 & 5.3

The Heat Recovery section shall include enthalpy wheels and shall have minimum recovery of 75 % of total heat, i.e. both sensible and latent (each being 75 %). The recovery of sensible and latent shall be equal. Necessary computerized selection of the wheel should be provided along with the bid to justify the same. The wheel shall be made of pure aluminium foil coated with molecular sieve desiccant with pore diameter of 3oA.The cross contamination between the two air streams shall be nil and leakage less than 0.04%. The vertical and radial run of the wheel shall be less than 1 mm per meter of diameter. The wheels shall have non-contact labyrinth seals for effective sealing between the two air streams.

# C.7.1 	Heat Recovery Wheel specifications

Rotor/wheel matrix shall be: -

1 	The substrate: The substrate or wheel matrix should be only of pure aluminum foil so as to allow:

1.1 quick and efficient uptake of thermal energy.

1.2 sufficient mass for optimum heat transfer

7.1.3 maximum sensible heat recovery at a relatively low rotational speed of 20 to 25 rpm.

2 	Non-metallic substrates made from paper, plastic, synthetic or glass fibre media, will therefore, not be acceptable.

3 	The substrate shall not be made from any material which is combustible or supports combustion like synthetic fibrous media.

4 	The wheel has to be certified as per DIN EN ISO 846 with 0% fungal and bacterial growth at 95% Relative humidity and above.

5 	Fire rating:

7.5.1NFPA - 90A certification with0% for Flame spread classification should be confirmed by manufacturer.

6 	Pressure Drop:

7.6.1The pressure drop across the rotary heat exchanger shall not exceed 0.1 inch for every 100FPM face velocity, or part thereof, for the minimum stated / required latent recoveries / efficiencies

7 	The Desiccant: The desiccant should be water molecule selective and non-migratory.

The desiccant should be molecular sieve 3Å, so as to keep the cross contamination to absolute minimum and also ensure the exclusion of contaminants from the air streams, while transferring the water vapour molecules.

The desiccant, of sufficient mass which should not be less than 5 kg per 1000 cfm of air, should be coated with non-masking porous binder adhesive on the aluminum substrate so as to allow quick and easy uptake and release of water vapour. A confirmation has to be provided by manufacturer of wheel to this effect. A matrix with desiccants impregnated in non-metallic substrates, such as synthetic fibre, glass fibre, etc. will not be accepted.

The rotor/wheel matrix shall have equal sensible and latent recovery.

The weight of desiccant coating and the mass of aluminum foil shall be in a ratio so as to ensure equal recovery of both sensible and latent heat over the operating range.

Accordingly, a rotor matrix which has an etched or oxidized surface to make a desiccant on a metal foil and results in insufficient latent recovery and hence unequal recovery, or a rotor matrix made from desiccant integrated in a synthetic fibre matrix which result in insufficient sensible recovery, high rotation speed, and unequal recovery, shall not be accepted.

8 	Rotor: With optimum heat and mass through matrix formed by desiccant, of sufficient mass, coated on an aluminum foil, the rotor should rotate at lower than 20 to 25 RPM, thereby also ensuring long life of belts and reduced wear and tear of seals.

8.1 The rotor shall be made of alternate flat and corrugated aluminum foil of uniform width.

8.2 The rotor honeycomb matrix foil should be so wound and adhered as to make a structurally very strong and rigid media which shall not get cracked, deformed etc. due to change of temperature or humidity.

8.3 The rotor having a diameter upto 2800 mm shall have spokes to reinforce the matrix. From

8.4 2000 mm diameter upwards, the option of a special wing structure, to prevent the rotors from wobbling or deforming due to the successive pressure differentials, will be available.

8.5 Sectioned wheels, with pie segments, capable of being assembled in the field, shall be available as an option, above 2000 mm in diameter.

8.6 The surface of the wheel/rotor should be highly polished to ensure that the vertical run out does not exceed + 1 mm for every 1 metre diameter, thereby ensuring, negligible leakage, if labyrinth non contact seals are provided, and minimal drag, if contact wiper seals are provided.

8.7 The radial run out also shall not exceed + 1 mm for every 1 meter diameter, thereby minimizing the leakage/drag on the radial seals, and minimize the fluctuation in the tension of the drive belt.

8.8 The number of wraps (of alternative corrugated and flat foil) for every inch of rotor radii shall be very consistent so as to ensure uniform air flow and performance over the entire face in the air stream. Flute height and pitch will be consistent to a very tight tolerance to ensure uniform pressure drop and uniform airflows across the rotor face.

8.9 The rotor shall be a non-clogging aluminum media, having a multitude of narrow aluminium foil channels, thus ensuring a laminar flow, and will allow particles upto 800 microns to pass through it.

8.10 The media shall be cleanable with compressed air, or low pressure steam or light detergent, without degrading the latent recovery.

9 	The Cassette / casing

9.1 The recovery wheel cassette/casing shall be manufactured from tubular / sheet metal structure to provide a self supporting rigid structure, complete with access panels, purge sector, rotor, bearings, seals, drive mechanism complete with belt.

9.2 The rotor/wheel should have a field adjustable purge mechanism to provide definite separation of airflow minimising the carryover of bacteria, dust and other pollutants, from the exhaust air to the supply air. It shall be possible, with proper adjustment, to limit cross contamination to less than 0.04% of that of the exhaust air concentration.

9.3 The face and radial seals shall be four (4) pass non-contact labyrinth seals / brush seals for effective sealing between the two air streams, and also for a minimum wear and tear ensuring long life of the seals.

10 Manufacturer / Principal

10.1 The manufacturer or their principals having at least 10 years’ experience directly in the product i.e. Energy Recovery Units (Treated Fresh Air Unit with Heat Recovery Wheel) with a two tier two air streams unit design in India shall be preferred. The Heat Recovery Wheel and the box should be from the same manufacturer.

# C.8	PRECISION AIRCONDITIONING UNITS

1.0 GENERAL

The room air-conditioning system shall be a floor discharge unit designed specifically for high sensible heat ratio applications such as Server and Computer rooms.

Each unit shall be capable of providing sensible cooling capacities at rated ambient temperatures with adequate airflow. Each unit shall be capable of required tonnage of cooling capacity and quantity of air flow as per Technical Specification when the room air-condition is 18+2 Degree Celsius and relative humidity is 50 + 5% R/H. The system shall contain Scroll compressor, Evaporator, Humdifier, Condenser and an Electronic Expansion Valve which shall be contained within the cabinet of the unit.

2.0 CABINET CONSTRUCTION

The frame and panels shall be constructed of heavy gauge Zinc-anneal corrosion resistant sheet steel. The fan section shall be insulated with minimum 25mm thick fire rated insulation. The cabinet shall be powder coated and have a textured finish.

3.0 EVAPORATOR COIL

The units shall be fitted with large surface area cooling coil with split coil mechanism for dehumidification. The evaporator coil shall be constructed of copper tubes and slit aluminium fins, with G.I frame and drip tray fabricated out of stainless steel. The cooling coil shall be a minimum of 3 row deep. The distance between the fins shall not be less than 1.8mm and face velocity shall be less than 2.3 mts./sec.

4.0 COMPRESSOR

The Compressor shall be of high efficiency Copelend make SCROLL design, with an

E.E.R. of not less than 11.0 BTU /Watt. Compressor shall have in built overloads, and shall be mounted on anti vibration mountings.

5.0 REFRIGERATION CIRCUIT

The refrigeration circuit shall be direct expansion type and incorporate hermetic scroll compressor. The system shall include a manual reset HP and an auto reset LP switch, filter drier and charging port. A thermal expansion valve, sight glass and filter drier shall be provided for each circuit.

6.0 FANS

The fan shall be backward curve centrifugal type, double inlet, double width, statically an dynamically balanced. Fan shall be driven by a high efficiency electronic commutated motor (EC Motor) with a self tensioning belt drive arrangement. The fan and motor assembly shall be mounted on anti-vibration mountings. Technical Specifications HVAC Works

7.0 HUMIDIFIER

Humidification shall be provided by boiling water in a polypropylene steam generator. The steam shall be distributed evenly into the bypass air stream of the precision air-conditioning unit. The humidifier shall be capable of providing 4.5 Kg. of steam per hour. The humidifier shall have an efficiency of not less than 1.3 Kg. per KW and be fitted with an auto flush cycle activated on demand from the unit’s control system.

The humidifier shall be fully serviceable with replaceable electrodes. Waste water shall be flushed from the humidifier by intitiation of water supply solenoid valve via a U pipe system.

8.0 ELECTRICAL HEATING

The electrical heating elements shall not operate at a level exceeding 60 W/Sq.m. The total heater capacity should not exceed 6.0KW. The heating circuit shall include dual safety protection through loss of air and high temperature controls.

9.0 SERVICE AREA

The unit shall be serviceable with a minimum service space of 900mm in front of the unit.

10.0 AIR FILTRATION

Filtration shall be provided by dry media disposable filters capable of filtering air to 95% (@5 micron) efficiency and shall be replaceable from the top of the unit.

11.0 AIR-COOLED CONDENSERS

The standard controls shall be factory matched to provide an operating range from 0 Degree Celsius to + 43 Degree Celsius. However, equipment can work upto +45 Degree Celsius under extreme conditions. Optional low ambient refrigeration controls (LARC) shall also be available to extend the operating range down to 1 Degree Celsius.

The condenser frame shall be constructed from heavy duty galvanised steel and incorporate copper tube and aluminium fin coil.

The coil shall be a minimum of 4 rows deep, with a minimum fin spacing of 2.0mm and maximum face velocity of 2.3 m/s.

The condenser fan(s) shall be directly driven by 1450 rpm electric motor(s) 4 pole.

12.0 CONTROLS

The standard controls shall be of microprocessor based programmable PID logic controller with Dew Point Logic. The controller shall have a LCD display screen, which shall be visible from the front of the unit without removing any covers / external panels.

The controls shall have separate indications for:

1)Various modes of operation (cooling, heating, humidifying and de-humidifying).

2)Alarm conditions (temperature high, wet floor and loss of air flow).

3)Digital displays of set temperature & humidity and achieved temperature and 	humidity.

4)Date, time and unit identification display.

5)Back up battery charge status display on the controller screen.

6)Visual system alarm indication (along with mutable audio alarm as well).

7)48 hrs. temperature and humidity graph display menu.

8)Programmable services interval indication display.

NIC Cards / other interfaces for BMS connectivity to be provided and shall be suitable to the protocol available / desired at client’s end.

The units shall be fully capable of being operated and monitored by IBMS System.

The system shall have a menu driven interface with supporting help screens and shall use multi-protocol data communications. Access to the controller settings shall be protected with passwords to prevent against unauthorized access. The unit should be able to transfer the controls to standby machine in even of fault. The controller should also incorporate 2 additional spare alarm inputs for customer interface (i.e. Unauthorized entry alarm, inputs for customer interface (e.g. Unauthorized entry alarm, building fire alarm etc.) manual override switches and selectable alarms. Local & remote alarms will be triggered in case of any alarm conditions being reached.

The unit shall also incorporate the following protections:

- Single phasing preventors.

- Reverse phasing.

- Phase imbalancing.

- Phase failure.

- Overload tripping (MPCB) of all components.

The units shall be so designed that only two units will operate at any time with automatic and schedule a rotation between the three units.

# C.9	SPLIT AIR CONDITIONING UNITS (HI- WALL TYPE)

1 	SCOPE

The scope of this section comprise the design, supply, erection, testing and commissioning of Air Cooled Packaged and Split Units conforming to these specifications and in accordance with the requirements of approved Drawings and Technical Specification.

2 	TYPE

The Split Units shall consist of hermetically sealed Scroll compressor, motor, air cooled condenser, sump heaters, integral refrigerant piping and wiring, all mounted on a steel frame.

Indoor unit to be installed for Split Unit within building, shall be housed in insulated cabinet consisting of cooling coil, blower with motor, filter & insulated drain pan.

The Air Cooled Packaged Unit shall consist of hermetically sealed Scroll compressor, motor, sump heaters, integral refrigerant piping and control panel duly wired to compressor and air cooled condenser all mounted on a steel frame.  The Air cooled condenser with fan duly mounted on a common frame shall be installed on the wall openings with suitable angle iron / channel frame to be provided by contractor.  The suitable starters, switches, power control cabling between Air Cooled Packaged Unit and Air Cooled Condenser shall be included by the contractor.

3 	CAPACITY

The refrigeration capacity of Packaged Unit and Room Air Conditioners, split unit shall be as per actual calculations and approved Drawings and Technical Specification.

4 	COMPRESSOR AND MOTOR

Compressor shall be hermetic reciprocating / Scroll, serviceable type and shall have dual pressure stat, and an operating oil charge. The motor shall be suction gas cooled and shall be sealed against dirt and moisture. The motor shall be suitable for 415±10% / volts or 230±10 % volts, 50 Hz, A.C. supply.

5 	REFRIGERANT PIPING AND CONTROLS

Refrigerant piping and fittings interconnecting compressor condenser shall be all copper and valves shall be brass / gunmetal construction.

6 	CASING

The indoor & outdoor units shall be sectionalised / cabinet construction. Indoor units shall be consisting of fan section, coil section, filter section, and drain pan. Outdoor unit shall consist of condenser coil, fan & compressor. In case of package units, the compressor shall be mounted within the indoor units and in case of split unit, the compressor shall be mounted with the outdoor units. Each section shall be constructed of thick sheet steel all welded / bolted construction, adequately reinforced with structural members and provided with sufficient access panels for proper lubrication and maintenance. Base panel shall be constructed of fabricated steel structure provided with an under frame suitably braced. Each unit shall include one piece drain pan constructed of 20 gauge galvanised sheet steel plate.  Drain pan shall extend under coil and fan sections with drain connections.  Removable panels in fan and coil sections shall provide access to all internal parts. Panels shall be internally lined with 2.5 cm thick fibreglass as per section “Insulation” for the thermal insulation and acoustic lining.

7 	FAN MOTOR AND DRIVE

Fan motor shall be suitable for 415 ± 10% volts or 230±10% volts, 50 Hz, A.C. Supply, Single phase, motors shall be provided with permanent capacitor.  Motors shall be especially designed for quite operation and motor speed shall not exceed 1440 rpm.

8	FAN

Fan wheels and housing shall be fabricated from heavy gauge steel. Fan wheels shall be of double-width, double inlet forward-curve, multi-blade type enclosed in a housing and mounted on a common shaft. Fan housing shall be made of die-formed steel sheets with stream-lined inlets to ensure smooth air flow into the fans, fan shaft bearing shall be oil/grease lubricated.  All rotating parts shall be dynamically balanced individually, and the complete assembly shall be statically and hydraulically balanced.  Fan speed shall not exceed 1000 rpm and maximum fan outlet velocity shall be 550 meters per minute.

9	COOLING COIL

Cooling coils shall be of fin and tube type having aluminium fins firmly bonded to copper tubes assembled in zinc coated steel frame. Face and surface areas shall be such as to ensure rated capacity from each unit and air velocity across each coil shall not exceed 100 meters per minute. The coil shall be pitched in the unit casing for proper drainage. Each coil shall be factory-tested at 21 Kg. per sq.cm air pressure under water. Tube shall be mechanically / hydraulically expanded for minimum thermal contract resistance with fins. The number of fins per cm. shall be 4 to 5.

10 	VIBRATION ISOLATORS

The indoor and outdoor units shall be provided with ribbed rubber pad vibration isolators.

11 	PAINTING

Split units shall be factory finished with durable alkyd spray enamel.  Shop coats of paint that have become marred during shipment or erection shall be cleaned off with mineral spirits, then coated with enamel paint to match the finish over the adjoining shop-painted surface.

12 	PERFORMANCE RATING

The unit shall be selected for the lowest operating noise level. Capacity rating and power consumption with operating points clearly indicated shall be submitted with the tenders and verified at the time of testing and commissioning of the installation.

# C.10	CHILLED WATER (HYDRONIC) CASSETTE UNITS

1.0 SCOPE:

Scope of this section covers the design, supply, installation, testing & commissioning of Chilled Water Cassette type fan coil units.

- GENERAL

The Chilled Water Cassette Units shall be concealed type, ceiling suspended type and shall be complete with fan, fan casing, fan motor, cooling coil made of copper tube and aluminium fins, filter, built-in condensate water pump, casing, insulated drain pan etc.

- DESCRIPTION & CONSTRUCTION

3.1 The unit shall be 4-way Cassette type. The unit shall comprise of coil section,3 speed motor, 4-dimension screw fan, circuit box, decorative panel, thermostatic controls, drain pump assembly, galvanized sheet steel casing with GI coated finish.

3.2 The Drain pump mechanism shall be ideally suited to lift water up to a height of 500 mm. The pump shall be inter-locked in such a way that if the drain pump mal functions, the unit shall stop functioning and give a warning signal.

3.3 The unit shall be fabricated from 18 Gauge G.I. sheets & ABS plastic.

3.4 The fan shall be slow speed statically & dynamically balanced directly driven forward cured. The fan shall be able to deliver air @ 400 CFM / TR at the high speed.

3.5 Fan motor shall be single phase suitable for 220 V, 50Hz A.C. supply & shall have at least 3 speeds operation.

3.6 Cooling coil shall be of copper pipe with min. 7mm O.D. and wall thickness of 0.4mm. Coil shall be min. 2 row deep. The coil shall be suitable for operation on chilled water and accordingly return headers shall be provided. The end connection shall be ¾”. The coil shall be hydrophilic aluminium type for prolonged life of equipment.

3.7 The units shall be with a cordless remote controller. The remote shall be able to control set temperature, fan speed and preferable timer on/ off.

- INSTALLATION:

4.1. The Chilled Water Cassette shall be suspended from the ceiling, using anchor fasteners for robust fitting. The unit shall be hung using threaded hangers for height and level adjustment. These hanging accessories have to be factory provided.

4.2. An auxiliary drain tray arrangement shall be provided to house the ball valves, strainer and on/off control valve assembly. Water from this aux. tray arrangement shall go back into the Cassette main drain tray and no additional drain pipe outlet shall be provided.

4.3. The connection between the Chilled Water Cassette and the valves shall be with 3/4” O.D. 22G heat treated copper tubes, insulated with tubular sections of atleast 12mm. The connection from the head pipe up to the valves may however be of MS class C piping with expanded polystyrene insulation duly provided.

4.4. A factory prepared valve station comprising of ball valve with strainer for inlet connection and ball valve without strainer and motorized 2 way valve for outlet connection shall be provided alongwith cassette units.

4.5. A onetime riser shall be provided for the drain flow to ensure no return of the drain water under any circumstances. A natural gravity slope shall be provided after the riser.

- CONTROLS:

5.1 The controls for Cassette Units shall consists of a combined thermostat and speed switch and motorized 2 way valve.

5.2 Water side inlet & outlet of the FCU shall be provided with Brass ball valves suitable for connection to M.S. ‘C’ Class threaded nipple on one side & flared copper connection on the other. The inlet value shall also be provided with a built-in Y – Type strainer.

  - A two way on/off diverting valve of recommended make shall be provided to facilitate regulation of temperature in the conditioned area. The value shall be suitable for 220 V, 50 Hz operation. The valve shall be on/ off type valve. No modulating function type valves shall be acceptable for the Cassettes.

- CAPACITY:

The capacity of the Cassette Units with respect to its TR and CRM shall be as given here  under :-

- 1.0 TR/ 400 CFM

- 1.5 TR / 600 CFM

- 2.0 TR / 800 CFM

- 2.5 TR / 1000 CFM

- 3.0 TR / 1200 CFM

- 3.7 TR / 1500 CFM

# C.11 THERMAL HEAT RECOVERY WHEEL

1	SCOPE

The scope of this section, comprises the design, supply, erection, testing and commissioning of Thermal Heat Recovery Wheel, conforming to these Specifications and in accordance with requirements of drawings and of the Technical Specification.

2	TYPE

The Thermal Heat Recovery Wheel shall be cabinet type construction, comprising of various sections such as supply air, exhaust air and fresh air connections as shown on approved drawings and included in Technical Specification.

3	CAPACITY

The Heat Recovery capacities, maximum motor horse power shall be as per approved Drawings and Technical Specification.

4	ACCESSORIES

a.	Wheel: The wheel shall be made of alternate layer of corrugated and intervening flat composite material of aluminium foil of uniform width to ensure smooth surface.  The wheel medium should be bonded together to form rigid transfer medium forming a multitude of narrow channels ensuring laminar flow.  The wheels shall be of proven design.

The wheel can be fully wound or on larger units, sectorised, i.e. assembled in segments.  In latter case the segments are assembled between rigid spokes thus ensuring structural longevity and allowing replacement of one or specific segments only.

The wheel shall be cleanable by spraying its face surface with compressed air, low temperature steam or hot water or by vacuum cleaning without affecting its latent properties.

The face velocity across the wheel should not exceed 700 fpm (3.5 m/s).

The wheels shall be tested in accordance with ASHRAE S4-78 method of testing air to air heat exchangers.  Development an manufacturers shall meet all quality assurance criteria specified in BSEN ISO 9001.

The minimum sensible and latent efficiencies should be 75%.  A computerized selection should be enclosed along with offer.

b.	Casing: The casing shall be constructed as a single skin, self-supporting, galvanized sheet steel structure and include rotary wheel support beams and purging sector.  The casing shall be supplied with access panels to facilitate inspection and service.  Size 2150 mm and larger shall be in two sections to facilitate shipping and handling.

c.	Seals: The casing shall be equipped with adjustable brush seals, which minimize the carryover to max 0.05 – 0.2%.

d.	Hub and Spokes: Hub and Spokes on one piece rotor shall be Aluminium and on sectorrized rotor Hub shall be made of steel, painted with ani corosion paint and galvanized sheet steel spokes.

e.	Drive : The wheel shall be belt driven along its perimeter.  A constant speed fractional horsepower motor shall be used.  The motor shall be mounted on a self-adjusting base to provide correct belt tension.

5	TESTING

The Thermal Wheel shall be tested in accordance with the parameters fixed as below.

i.  	Supply Air Capacity - FDB/FWB.

ii. 	Exhaust Air Capacity - FDB / FWB.

iii. 		Fresh Air Capacity - FDB / FWB.

# C.12	SCRUBBER UNIT – DRY SCRUBBERS

1	SCOPE

The scope of this section comprises the design, supply, erection, testing and commissioning of dry scrubbers comprising of electrostatic sections with auto wash module for use in kitchen exhaust / grease / exhaust air treatment.

2	TYPE

The unit shall be CE certified and of the type as per approved Drawings and Technical Specification.

3	CAPACITY

The air-moving capacity of unit shall be as per approved Drawings and Technical Specification.

4	TECHNICAL PARAMETERS

The unit shall provide efficiency of 90% or better for single pass base on ASHRAE test method at flow rates of 800 – 1300 CFM per module (supported by sample test report by a US laboratory).  Multiple units can be joined together for increased volume.  The system shall be suitable to connect to fan section with average velocity of 500 FPM across air cleaner.

5		EQUIPMENT SPECIFICATIONS

The unit shall be designed and constructed and supplied by a manufacturer specializing in the research, design and manufacture of products specified in this section with a minimum of three years of documented experience, and capable of issuing complete catalog data on the total product.

6		UNIT HOUSING

Housing shall be 16-gauge zinc coated steel construction to protect against rust and corrosion.  Each section shall include single door access, located one side of the unit.  The access door shall be mounted on steel hinges and secured with adjustable, gasket sealed lever latches allowing for component access and removal.  All doors shall be gasketed to prevent air and water leakage. Doors to charged high voltage components shall be equipped with electrical interlocks, for interconnection into the primary power supply, to prevent access when the components areenergized.  The housing shall be furnished completely assembled for ease of shipment and installation.  Between each section, a permanent 1/8” thick gasket shall be installed to prevent leakage.  The bottom drain pan under ESP section containing integral washing systems shall be pitched downward 1/4“ per foot minimum toward a 3” NPT drain nipple.

7	BASE CONSTRUCTION

The sections are to be mounted on a structural C-channel or floor mounting or ceiling suspension.  Lifting lugs shall be incorporated in the base channel to allow for rigging, if ordered.

8		FINISH

The external casing finish shall be a durable industrial grade semi gloss baked-on epoxy ester, not less than 3 mil minimum thickness.

9		CELLS WASH MODULE

The Cells Wash module shall incorporate mechanical filtration.  The stationary filter from the direction of airflow will be a metal mesh filters with single, gasketed access doors. Wash manifolds and headers are supplied to wash the module during the normal wash cycle.

10		ELECTROSTATIC PRECIPITATOR MODULE

The electronic air cleaner shall be the two-stage dual voltage plate type cells, rated at not less than 90% efficiency as per the ASHRAE test standards for dry particulate (supported by sample test report by a US laboratory).The collection cells shall be in Single Pass arrangement to provide for maximum collection efficiency.

11		IONIZING COLLECTION CELL

Ionizing-Collecting cell(s) shall be of one-piece construction 14.23” inches deep in direction of airflow.  All support framing, end plates and ionizer ground electrodes shall be 0.090 inch thick aluminum.  Both repelling and collector plates shall be 0.020 inch thick aluminum, 9.125 inch deep in direction of airflow and rigidly retained in place with tubular spacers and tie rods.  Spacing between plates shall be no less than 0.175 inch.  Ionizing electrodes shall be 24 gauge stainless steel spiked design, ionization wires are not acceptable, rigidly supported both vertically and laterally. High voltage support insulators shall be of self-glazing Cordierite ceramic with all surfaces, including center hole, glazed to enhance dielectric strength and retard tracking.  Insulators shall be mounted out of the airstream, to reduce contaminant buildup. All high voltage electrical connections within each tier of cells, shall be between cells and automatically made when cells are installed.  All electrical connections between unit tiers and high voltage connections between power packs and cells shall be located on the access door end of the cabinet and manually connected for ease of service.

12	POWER SUPPLIES

Power supplies shall be 100% solid state, UL Listed. operate on 200 to 240 VAC, 50 HZ, 1 Phase input and provide a dual high voltage output of (+) 12 to 13 KVDC for the ionizer and (+) 6.0 to 6.5 KVDC for the collector.  A regulated output of up to 5.5 MA shall be supplied to maintain the specified collection efficiency.  Integrally mounted electrical interlocks shall be provided to prevent access to the high voltage components without first interrupting the primary input power.  The power supply shall operate over a temperature range of -32 degrees F to 140 degrees F, be self-protecting and accommodate an LED light indicating the performance status of the ionizing/collecting cell. High voltage output leads shall be sealed and a bleed resistor incorporated to remove stored electrical charge where the power supply(s) are de-energized. Module of capacity above 3000 CFM  shall be equipped with Pulse width modulating (PWM) to maintain the specified collection efficiency by maintaining a constant charge in the event of Low/High Voltage from source thus ensuring that the unit functionality is not affected with these voltage fluctuations. Power Consumption should not be more that 50 watts per ESP cell.

All power supply components shall be designed for ease of mounting and servicing. High voltage power cables shall be of one continuous length, splicing is not acceptable.

13		SYSTEM CONTROLS

Programmable Logic Controller (PLC) shall be housed in a NEMA-12 type enclosure.  Controller shall be shipped for remote mounting and must be installed indoors or other means of weather protection provided if installed.  Terminals shall be provided to interconnect the system fan and shall sequence the detergent wash, soak, rinse fan force dry and return to operation cycle.  All sequence times shall be factory set.  Control initiation shall be semiautomatic, push button initiated, or fully automatic by time clock, with semiautomatic push button override.

A remote mounted Sleep Mode Reset Switch (momentary contact push button type) shall be supplied to be installed at the kitchen hood location to re-energize the air cleaning system after the wash system has completed. The switch may optionally be installed on the panel of the ATS control enclosure.

14		AUTOMATIC TIME CLOCK

The control cabinet shall be furnished with a factory installed and wired 7-day initiator clock with battery backup.

15		WATER WASH/DETERGENT SYSTEM

Detergent wash and rinse will be accomplished with manifolds located on the air entering sides of the (prefilter wash collar if supplied) ionizing/collecting cell tier through spray nozzles delivering a cone shaped pattern.  The detergent reservoir, pump, motor and bypass valve shall be provided as a prepackaged assembly with an adjustable detergent volume setting.  The detergent pump motor shall be 0.75kW TEFV motor, 220v/50hz/1ph, with pump of positive displacement self priming and deliver not less that 6 GPM at 50 PSIG minimum outlet pressure.  Pump motor shall contain built-in overload protection.  Main water line strainer and solenoid valves are to be factory furnished with the system.  Detergent system shall a 30-gallon tank for remote mounting with initial supply of biodegradable detergent as per unit manufacturer’s recommendations.

16	STATIC PRESSURE DROPS

The pressure drop shall not exceed the following (inches H2O):

ESP Section						0.14”

Metal Mesh prefilter or after filter				0.10”

The ESP section must have both an internal prefilter and an after filter, select and add for each.

External losses for ductwork, exhaust hoods, manufacturing equipment with associated entry losses, kitchen hoods, etc.. must be added with the above internal equipment losses to calculate total fan static pressure required.

17	ADSORBER MODULE

The Adsorber Module shall be designed to utilize required number of 23.38” x 23.38” x 2” deep trays that are powder painted for corrosion resistance, may be reused and are secured in a V-bank arrangement on steel slide tracks.  Trays shall be charged with 18.25 lbs. of activated carbon granules.

# C.13 	Axial / Centrifugal / Propeller / Inline / Roof Mounted Fans

1	SCOPE

The scope of this section comprises the design, supply, erection, testing and commissioning of centrifugal,  in-line   and propeller  type  fans and roof mounted  units  conforming  to these  Specifications and in accordance with the  requirement of approved Drawings and Technical Specification.

2	TYPE

Centrifugal, in-line propeller fans and roof mounted units shall be of the type as indicated on approved Drawings and as per Technical Specification.

3	CAPACITY

The air-moving capacity of fans shall be as per approved Drawings and Technical Specification.

4	AXIAL FLOW FAN

The Exhaust air Blower shall be Tube Axial Fans connected to the duct & shall be of floor/ Ceiling /wall mounted type. The Capacity of Tube Axial Fan, diameter, maximum motor H.P. & Static Pressure etc. shall be according to actual calculations, technical specifications and approved drawings. The Noise Level of Axial fan shall be less than 80 dBA at a distance of 3.0 mtr from the fan.

Axial Flow Fan shall be AMCA Certified (FEG Grade) for Air and Sound Performance in accordance to AMCA 210 and AMCA 300.

The cylindrical casing shall be made from MS/GI welded carbon steel sheet. The Length of of casing shall be long to accommodate motor within the casing. Casing thickness shall be minimum 2mm up to 800 mm dia. and 3 mm thick from 900 to 1250 mm dia. & 4 mm thick above 1300 mm dia. the Inlet & Outlet of the casing shall be fitted with flanges for ductwork connection & other accessories as required.  The casing shall be coated with minimum 2 coats of rust proof primer and enamel paint thereafter or to be powder coated after phosphating process. The Blade of Axial flow fan shall be made of die cast aluminum alloy. The blade angle shall be set at manufacturing place & shall be adjusted at site. The Hub shall consists of two half hubs pressed in carbon steel &the centre boss shall be made of die -cast aluminum alloy. The Blade feet shall be locked in two half-hubs. The design shall facilitate the alteration of blade angle without disconnecting the hub from the motor shaft. The fan shall be directly driven by TEFC Sq. Cage induction motor. The fan motors shall be 415 +10%volts 50HZ+5%, 3 Phase TEFC Sq. Cage Induction motor. The motor shall be specially designed for quiet operation & Motor RPM shall be as per OEM.

Complete Fan with motor shall withstand 250 °C temperature for 2Hours & shall work satisfactorily at this temperature. Motors selected for this application shall be UL Recognized.

Complete Fan assembly for Smoke extraction application (Fan Impeller, Fan Casing, Motor Base frame along with motor) shall be tested and approved by UL in accordance with "Power Ventilators for Smoke control systems" for 250 degree Celsius temperature for 2Hours of operation.

Vibration Isolation: The assembly of fan and motor shall be suspended from the slab by vibration isolation suspension of heavy duty spring isolators type.

Accessories: The following accessories shall be provided with all fans :

i.	Outlet cone for static pressure regain.

ii.	Inlet cone.

Fan silencers may be provided where specifically called for in Technical Specification. Fans shall be factory assembled and shipped with all accessories factory-mounted.

5.	PROPELLER FAN

Propeller fan shall be direct-driven, three or four blade type, mounted on a steel mounting plate with orifice ring.

a.	Mounting Plate shall be of steel construction, square with streamlined venturi  inlet  (reversed  for  supply applications)  coated with baked enamel paint.  Mounting plate shall be of standard size, constructed of 12 to 16 gauge sheet steel depending upon the fan size. Orifice ring shall be correctly formed by spinning or stamping to provide easy passage of air without turbulence and  to direct the air stream.

b.	Fan  Blades  shall be constructed of aluminium or  steel. Fan hub shall be of heavy welded steel construction  with blades  bolted  to the hub. Fan blades and  hub  assembly shall  be  statically  and dynamically  balanced  at  the manufacturer’s works.

c.	Shaft  shall be of steel, accurately ground and shall  be of ample size for the load transmitted and shall not pass through  first  critical  speed thru the  full  range  of specified fan speeds.

d.  	Motor   shall be standard (easily replaceable) permanent split  capacitor or shaded pole for small sizes,  totally enclosed  with  prelubricated sleeve  or  ball  bearings, designed for quiet operation with a maximum speed of 1000 rpm for fans 60 cm dia or larger and 1440 rpm for fans 45 cm  dia  and  smaller. Motors for larger  fans  shall  be suitable  for  415±6% volts, 50 cycles 3  phase  power supply, and for smaller  fans shall be suitable for 220 ± 6%  volts, 50 cycles single phase power  supply.  Motors shall  be  suitable  for either  horizontal  or  vertical service  as  indicated on approved Drawings and  technical specifications.

e.	Accessories: The following accessories shall be provided  with  propeller  fans :

i.	Wire guard  on inlet side and  birdscreen  at  the outlet.

ii.	Fixed or gravity louvers built into a steel frame at the outlet.

iii.	Regulator  for controlling fan  speed  for  single phase fan motor.

Iv	Single phase preventors for 3 phase fans.

6.	Circular Mixed Flow Inline Fan

Circular Mixed Flow Inline fan shall incorporate dual speed Mixed Flow direct driven ABS Impeller for high pressure & low noise level. The fan assembly shall be encased in shockproof & corrosion resistant casing along with connection box. The fan casing shall be of High Grade plastic material.

The Fan can be easily mounted on ceiling and mounting frame shall be provided to facilitate easy connection and access to the fan/impeller without dismantling the duct for maintenance & cleaning purpose. Flexible anti-vibration joints shall be provided to arrest vibration being transformed to other equipment connected to inline fan. Motor shall be dual speed, single phase having IP44 protection with sealed ball bearing.

The Fan should be installed along with wired plug and 2 speed controller should be wired in connection box for easy electrical connection at site.

7.	Cabinet Inline Fan

Cabinet Inline fan shall incorporate DIDW direct driven centrifugal fan with TEFC (IP-44) motor. The cabinet fan assembly shall be encased in sheet metal housing of heavy gauge construction with acoustic lining for low noise level and with necessary inspection cover with proper gasket assembly. The fan material shall be of galvanized sheet. Flanges shall be provided on each side of the inline fan to facilitate easy connection. Flexible anti-vibration joints shall be provided to arrest vibration being transformed to other equipment connected to inline fan. Motor shall be single phase as mentioned in technical specification.

All cabinet fan shall be provided with three speed regulator along with opposed blade dampers in GSS construction at fan outlet for air balancing.

8.	ROOF MOUNTED FAN

Roof mounted fan shall be propeller type or centrifugal fans, direct driven or belt driven as shown on approved drawing and Technical Specification, complete with motor drive, and housing with weather-proof cowl.

a.	Housing: shall be constructed of 16 gage steel sheet. The housing  shall  have an adjustable flange  to  facilitate installation  and shall be especially adapted to  receive fan,  motor,  and  drive. The housing shall  have  a  low silhouette.   For  belt  driven  units,  motor  shall   be installed  in ventilated water proof housing outside  the air stream. The discharge cowl shall be hinged along  one edge  for easy access to motor and drive, for  inspection and   maintenance.   The   entire   assembly   shall   be  weatherproof   and   raised   from   the   roof   terrace   sufficiently   to   prevent  downflow   of   rain   water accumulated on the terrace. 18 gage galvanized steel mesh birdscreen shall be  provided  on  all discharge cowls around the outlet area.

b.	Fans : shall be backwardly inclined centrifugal wheel  or propeller   type  as  required,  designed   for   maximum efficiency,  minimum turbulence and quiet operation.  Fan shall be statically and dynamically balanced.

c.	Motor : shall  be shaded pole,  of split  capacitor  type with  lubricated  sleeve or ball bearings,  designed  for quiet operation. Bearings shall be designed for  vertical mounting.  Motor  name-plate horse-power shall  be  such that  the  motor shall not be overloaded  in  the  entire range  of  rated speed. Motor and fan assembly  shall  be easily  removable. Motor power supply characteristic  and maximum  speed shall be as specified for  propeller  fans and as indicated in the Technical Specification.

d.  	Fan  Bearings :  shall  be  heavy  duty,  self   aligning sleeve/ball bearings designed for thrust load and  sealed for grease retention.

e.	Backdraft  Damper : Roof-mounted  fan shall be equipped with  a rattle-free  backdraft  damper to prevent  air  from  re-entering  the  fan  when fan is not  in  operation,  thus sealing  completely in closed position. Damper  shall  be chatterproof under all conditions.

f.	Vibration Isolation : The motor and fan assembly shall be isolated  from the base with   vibration isolators.

# C.14	BASEMENT/CAR PARK VENTILATION & SMOKE EXTRACTION FANS

1	System description and functional responsibilities

The contractor shall provide a basement/car park ventilation system that is consistent with the scheme as indicated on the drawings.  The system shall serve both CO evacuation and smoke extract function.

The contractor shall provide a full Owner/PMCing proposal that includes the following information for review by the Owner/PMC-in-charge.

Specification, manufacturer’s data and performance data for all devices and equipment to be utilized in the system.

Control schematic for operation of the system.

All ancillary devices such as motorized dampers, silencers, smoke detectors, CO detectors, etc. that are required to ensure proper system operation in both the CO and smoke modes.

All necessary devices that are required to interface with the base building systems such as fire alarm and detection BMS etc.

The system principles are as follows:

Smoke control designed to provide such a much safer Owner/PMCed system.

Fully automatic smoke control.

Lower the air temperatures during fires.

Total ductwork distribution.

Improved fire fighting access.

High air movement preventing fire spread.

Efficient cross ventilation.

2	System description

The main extract fan shall be axial fans mounted in parallel.  All fans shall be located close to risers as shown in the drawings.

Under “normal” ventilation conditions, normal case running exhaust fans (equivalent to 6 ACPH) shall be ON. In case of fire, normal working fans (6 ACPH) + Fire fans (additional 6 ACPH) shall be ON.

Fire / Smoke detection shall be based upon multi-criteria smoke detector which shall indicate the area in which the fire is located.  Upon detection the main extract fans shall operate at full speed, increasing the airflow on the fire floor.  The control system shall determine set of extract fans to be activated to contain the smoke.

All fans in car park and for smoke extraction shall be rated to withstand a temperature rating of 2500C for a period of 2 Hour.  The cable supplying the power to these fans shall also be fire rated.  The entire fan including motor, terminals and incoming cables shall also be suitable for 250 deg C for a period of two hours.

The car park ventilation system shall be a standalone life safety system.  The control system shall be of the intelligent PLC type assuming control of both carbon monoxide and smoke evacuation

3	CO Detection

The car park ventilation systems shall be controlled by an individual CO-Monitoring system for entire car park located on each level to optimize efficiency.  The contactors within the motor control panel shall be controlled by a Carbon Monoxide monitoring panel which shall contain DDCs (Direct Digital Controllers) where the pre-determined switching strategy and logic shall be loaded.  The CO monitoring panel shall receive signals from CO sensors located throughout the levels at a spacing of no. more than 1 per 350 m2.  The 24Vac power supply for the CO sensors shall be mounted in the same panel.  The power supply shall be looped across the CO sensors. The proposed CO sensor shall provide a 0-10 VDC signal for measuring the CO level in the car park area.

CO monitoring devices shall be mounted remotely throughout the car parks.  The devices shall be mounted in accordance with the manufacturers guidelines but no greater than 1.5 m above FFL.

The contractor should refer to the specific requirements of the sensor supplier for quantities of CO-detectors.

4	CO Sensor

The sensor shall be suitable for wall mount & capable of following features:

Digital display of the CO level : 0 to 200 ppm

Analog output : 4 to 20 mA / 0-10VDC

Low Voltage operation : 24 VAC / VDC

Wall Mount Configurations

Test Switch : Provides mode for system self test.

Automatic Calibration (Field Calibration Kit)

Over-range indication.

Start-up mode : steps display and output through test ranges.

Solid – Stat sensor : Life expectancy of 7 to 10 years.

Multiple sensors with one power supply.

Carbon monoxide sensor shall comprise of a carbon monoxide meter and a 4-20mA/ 0-10 VDC transmitter an all electronic system that utilizes a microprocessor to measure carbon monoxide (CO) levels, calculate various calibration factors and analog output.  The sensor shall averages samples over a time period and updates the output every 2 ½ minutes.  The sensor shall be intended to be used in enclosed parking garages, where it provides CO data to building automation computers or controllers.  A UL knockout box shall house the sensor and provide an easy-to-mount, study housing for the system.

Sensors shall be mounted on walls or columns about 1600 mm above the floor.

Sensors shall be evenly spaced and not put in corners, or directly in front of air inlets.

Each sensor must have a cable directly to the control panel.

In addition to above CO-sensor shall comply with following :

Power 				24 VAC / VDC @ 150 mA

Colour				Gray

Measurement range		0 to 200 ppm of CO (4-20 mA)

Electrical class			General Purpose, non-hazardous.

Operating temperature range	0 deg. To 125 deg.F (-18 deg.To 52 deg.C)

5 	Fire / smoke detection

The car park ventilation system shall be designed based on 12 ACPH in fire mode.

The car park ventilation system shall interface with the fire alarm control panel to receive signals from the detectors.

The Contractor shall be responsible for the full integration of the fire alarm and car park ventilation control systems.

6	 Control Panels

The manufacturers Owner/PMCed solution shall allow for a stand alone intelligent PLC control system for both CO monitoring and smoke control. Each car park shall have individual PLC Control Panel.  The PLC control system shall be seperate for each level of entire car parking and shall control all exhaust fans located on each level.  The broad logic shall be as follows:

PLC based Logic panel shall be provided to receive signals from the Carbon Monoxide Detector panel and the Fire Control Panel which will contain DDC (Direct Digital Controller) to give command to Exhaust fans for their operation on the basis of the logic provided to the PLC panel as shown below:-

Condition 1:Under normal ventilation condition, air shall be drawn through all parts of the car park by the Axial fans (operating at low speed) at a rate equivalent to 6 air changer per hours.

Condition 2: When the CO level rise beyond 25 ppm the fans shall start at low speed.

Condition 3: If the CO level continue to rise to the high limit set value to 35 ppm, the makeup fans and extract fans shall operatre at high speed to provide a rate equivalent to min. 6 air changes per hour.

Condition 4: In the event that Smoke is detected in the car park a priority Signal shall be provided by the fire detection panel which shall switch the car park ventilation system to smoke extract mode.  The makeup fans will be started at full speed in order to dilute the dense smoke and smoke extract fans shall operate at full speed.

7	PERFORMANCE DATA

All  fans  shall be selected for the lowest  operating  noise level.  Capacity  ratings, power consumption,  with  operating points clearly indicated, shall be submitted and verified  at the time of testing and commissioning of the installation.

8	TESTING

Capacity of all fans shall be measured  by  an  anemometer.  Measured air flow capacities shall conform to the specified capacities and quoted ratings. Power consumption shall be computed from measurements of incoming voltage and  input current.

# C.15	PIPING WORKS

1	SCOPE

The scope of this section comprises the design, supply and laying  of pipes,  pipe fittings and valves, testing and balancing  of all  water and refrigerant piping required for  the  complete installation.. All piping inclusive of  fittings  and valves shall follow the  applicable  Indian Standards. All welders used for piping erection shall be well qualified (certificate should be submitted to Owner/PMC-in-charge for approval) and shall have minimum 8 to 10 years experience.

2	PIPE SIZES

Pipe  sizes  shall be as required for  the  individual  fluid flows.  Various  pipe  sizes  have  been  indicated  on   the Drawings, these are for Contractor’s guidance only and  shall not relieve contractor of responsibility for providing smooth noiseless balanced circulation of fluids.

3 	GROOVED PIPE JOINTING SYSTEM

- References:

  - American Society for Testing Materials (ASTM)

    - ASTM A-53 – Pipe, Steel, Black and Hot-Dipped Zinc Coated, Welded and Seamless.

    - ASTM A-183 – Carbon Steel Track Bolts and Nuts

    - ASTM A-234 – Standard Specification For Piping Fittings or Wrought Carbon Steel and Alloy Steel.

    - ASTM A-449 – Quenched and Tempered Steel Bolts and Studs

    - ASTM A-536 – Ductile Iron Castings

    - ASTM F-1476 - Standard Specification for Performance of Gasketed Mechanical Couplings for Use in Piping Applications

  - American Society of Mechanical Owner/PMCs

    - ASME B16.9 – Factory Made Wrought Butt Welded Fittings

    - ASME B31.1 – Chemical Plant and Petroleum Refining Piping

    - ASME B31.9 – Building Services Piping

  - American Water Works Association

    - AWWA C-606 – Grooved and Shouldered Joints

- Quality Assurance

1.	All grooved components (including couplings, fittings, valves and accessories) to be supplied by one manufacturer.  Grooving tools shall be of the same manufacturer as the grooved components.

- Grooved Mechanical Couplings for Joining Carbon Steel Pipe

1.	Grooved Mechanical Couplings: Manufactured in two segments of cast ductile iron, conforming to ASTM A-536, Grade 65-45-12. Gaskets shall be pressure-responsive synthetic rubber, grade to suit the intended service, conforming to ASTM D-2000. (Gaskets used for potable water applications shall be UL classified in accordance with ANSI/NSF-61 for potable water service.) Mechanical Coupling bolts shall be zinc plated (ASTM B-633) heat treated carbon steel track head conforming to ASTM A-449 and ASTM A-183, minimum tensile strength 110,000 psi (758450 kPa) as provided standard Victaulic.

- Rigid Type: Coupling housings with offsetting, angle-pattern bolt pads shall be used to provide system rigidity and support and hanging in accordance with ANSI B31.1, B31.9, and NFPA 13.

- Flexible Type: Use in locations where vibration attenuation and stress relief are required. Flexible couplings may be used in lieu of flexible connectors at equipment connections. Three Couplings shall be placed in close proximity to the vibration source.

2.	Flange Adapters: For use with grooved end pipe and fittings, for mating to ANSI Class 150 flanges.

3.	Grooved couplings shall meet the requirements of ASTM F-1476.

4.	Gasket: Synthetic rubber, wide width, conforming to steel pipe outside diameter and coupling housing, manufactured of elastomers as designated in ASTM D-2000.

5.	Grooved End Fittings: Fittings shall be cast of ductile iron conforming to ASTM A-536, Grade 65-45-12, forged steel conforming to ASTM A-234, Grade WPB 0.375" wall (9,53 mm wall), or fabricated from Std. Wt. Carbon Steel pipe conforming to ASTM A-53, Type F, E or S, Grade B. Fittings provided with an alkyd enamel finish or hot dip galvanized to ASTM A-153.  Zinc electroplated fittings and couplings conform to ASTM B633.

Grooved Hole-Cut Branch Outlets:

- Bolted Branch Outlet: Branch reductions on 2"(DN50) through 8"(DN200) header piping. Bolted branch outlets shall be manufactured from ductile iron conforming to ASTM A-536, Grade 65-45-12, with synthetic rubber gasket, and heat treated carbon steel zinc plated bolts and nuts conforming to physical properties of ASTM A-183.

b.	Strapless Outlet: 1/2"(DN15) or 3/4"(DN20) NPT outlet on 4" (DN100) and larger header sizes rated for 300 PSI (2065 kPa).

c.	Strapless Thermometer Outlet: To accommodate industrial glass bulb thermometers with standard 1-1/4"-18 NEF 2B extra fine thread and 6" (152mm) nominal bulb length on 4" (DN100) and larger header sizes rated for 300 PSI (2065 kPa).

- CHILLED, HOT AND CONDENSING WATER PIPING

a.	Following material shall be used for pipes and fittings.

| Pipes Nominal size (mm) | Material Specification |
| --- | --- |
| <150 | IS 1239 Part-1 |
| 200 and above | IS3589Gr.FE410(8mmthick) |
| Fittings Nominal size(mm) | Material Specification |
| 25-300 | . Standard Grooved end Fittings (Elbows, Equal Tees, Reducers, Reducing Tees, Mechanical Outlets, Flanges etc.). |
| 350-400 | AGS Grooved end Fittings (Elbows, Equal Tees, Reducers, Reducing Tees, Flanges etc.). |
| > 450 | Site fabricated with AGS Grooved end (Elbows, Equal Tees, Reducers, Reducing Tees etc.). |
| Flanges Nominal size (mm) | Material Specification |
| < 65-300 | Standard Grooved end Flanges |
| 350-400 | AGS Grooved end Flanges |
| >200 | IS 2062 Gr.A, as per ANSI B16.5 (#150 class) |

All jointing in the pipe system shall generally be by Grooving, unless otherwise mentioned, or directed at site. All welding shall be done by qualified welders and

shall strictly conform to BIS Code of practice for manual metal arc, welding of Mild Steel.

b.	Groove Coupling:

1.	Pipes from 25mm to 300mm to be joined with Standard Grooved Couplings.

2.	Pipes from 350mm and above to be joined with two piece AGS (Advanced Groove System) Grooved Couplings only for better end load capability.

c.	Groove Fittings:

1.	Pipes from 25mm to 300mm to be of Grooved type should be joined with Grooved end Fittings (Elbows, Equal Tees, Reducers, Reducing Tees, Mechanical Outlets, Flanges etc.).

2.	Fittings (Elbows, Equal Tees, Reducers, Reducing Tees, Flanges etc.) for Pipes from 350mm to 400mm to be of AGS Grooved type. Fittings above 400mm to be site fabricated with AGS Grooved ends for better end load capability.

d.	Groove Tooling:

1.	Tools shall be manufactured and supplied by Single groove fitting supplier. Roll sets compatible with the pipe material and wall thickness as per manufacturer installation instructions  Manual to be used

2.	Common wedge shaped AGS groove for pipe sizes 14” (DN350) through 40”(DN1000).

e.	Grooving and Assembly Execution:

Installation:

- Pipe ends shall be clean and free from indentations, projections and roll marks in the area from pipe end to groove for proper gasket sealing.

- The gasket style and elastomeric material (grade) shall be verified as suitable for the intended service as specified.

- Install the AGS piping system in accordance with the latest installation instructions.

- AGS products shall not be installed with standard grooved end pipe or components.

- Use grooving tools with AGS roll sets to groove the pipe. Guidelines for tool selection and operation to be followed.

- Couplings installation shall be complete when visual metal-to-metal contact is reached.

f.	Training:

- Trained representative from manufacturer shall provide on-site training to contractor’s field personnel on the use of grooving tools, application of groove, and product installation.

g.	Application:

- Trained representative from manufacturer shall periodically visit the job site and review installation. Contractor shall remove and replace any improperly installed products.

- Grooved mechanical pipe couplings, fittings, valves and other grooved components may be used as an option to welding, threading or flanged methods.

- COLD WATER AND DRAIN PIPING

a.	All  pipes  to  be used for  cold  water (makeup),  drain, condensate  drain and fittings shall be GI / C-PVC as indicated in SPECIFICATION.

b.  	All   jointing   in   the  pipe  system   shall   be   by screwed  joints and/or by screwed flanges using  3  mm  3  ply  rubber insertion gaskets.  Pipe  threads  and flanges shall be as per relevant BIS Codes.

c.	All  pipes  supports  shall  be  mild  steel,  thoroughly cleaned  and  given one primary coat of red  oxide  paint before being installed.

d.  	Fittings   shall  be  galvanized  steel  `medium   class’ malleable  casting  of pressure rating suitable  for  the piping system. Flanges shall be of approved make.  Supply of   flanges  shall  include  bolts,  nuts,  gaskets   as  required.  Sufficient number of flanges and unions  shall  be provided for future cleaning and servicing of  piping. Tee-off  connection  shall be through equal  or  reducing  tees. All equipment and valve connections, or connections to  any  other  mating pipes  shall  be  through  flanges required for the mating connections. Fittings & flanges shall form part of piping and are not separately identified in Technical Specification.

e.	Gate  valves,  globe valves, check valves  and  strainers shall   be  similar  to  those  specified  for   chilled, condensing and hot water piping.

f.	For proper drainage of AHU Condensate, ‘U’ trap shall be provided in the drain piping.

g.	All  condensate  drain  piping  shall  be  insulated  and painted  as per the section “Insulation” as indicated  in Technical Specification.

- REFRIGERANT PIPING

a.	All  refrigerant pipes and fittings shall be  hard  drawn copper  tubes  and wrought copper / brass fittings  suitable for  connection with silver solder / phos-copper.

b.	All  joints in copper piping shall be sweat joints  using low  temperature brazing and / or silver  solder.  Before jointing any copper pipe or fittings, its interiors shall be  thoroughly cleaned by passing a clean cloth via  wire or  cable through its entire length. The piping shall  be continuously  kept clean of dirt etc. while  constructing the  joints. Subsequently, it shall be  thoroughly  blown out using carbon  dioxide / nitrogen.

c.	Refrigerant  lines shall be sized to limit pressure  drop between  the evaporator and condensing unit to less than  0.2 kg per sq.cm.

d.	Sight glass with moisture indicator and removable  type  combination  dryer cum  filter  with  MS housing  and brass wire mesh / punched brass sheet  shall be  installed in liquid line of the refrigeration  system incorporating a three valve by pass. After ninety days of operation, liquid line drier cartridges shall be replaced.

e.	Heat exchanger shall be  MS heavy duty pipe in pipe type and without any joint in the inner pipe.

f.	Horizontal suction line shall be pitched towards the compressor and no reducers shall be provided for proper oil return.

g.  	After  the  refrigerant  piping  installation  has   been completed,   the  refrigerant  piping  system  shall   be  pressure  tested  using  Freon  mixed  with  nitrogen   / carbondioxide  at  a pressure of 20 kg  per  sq. cm  (high side)  and 10 kg per sq. cm (low side). Pressure shall  be maintained  in the system for a minimum of 12 hours.  The system shall then be evacuated to a minimum vacuum of  70 cm  of mercury and held for 24 hours. Vacuum shall be checked with a vacuum gage.

h.	All refrigeration piping shall be installed strictly as per the instructions and recommendations   of   air conditioning equipment manufacturer.

- PIPING INSTALLATION

a.	Design Drawings indicate schematically the size and location of pipes. The Contractor, on award of the work, shall prepare detailed shop drawings, showing the cross-section, longitudinal sections, details of fittings, locations of isolating and control valves, drain and air valves, and all pipe supports. He must keep in view   the specific openings in the building through which pipes are designed to pass.

Pipe shall be cut only with hack saw blades and welding rods shall not be used for this purpose. All the pipes shall be cleaned and applied with one coat of Zinc chromate primer.

b.	Wire Hangers shall be used to suspend all static HVAC & Mechanical services.

1.	Wire Hangers should consist of a pre-formed wire rope sling with a range of end fixings to fit various substrates and service fixings, these include a ferruled loop, permanently fixed threaded M6 (or M8, M10) stud, permanently fixed nipple end with toggle, at one end or hook or eyelet, cladding hook, barrel, wedge anchor, eyebolt anchor or any other end fixture type or size as per manufacturers recommendation and design. The end fixings and the wire must be of the same manufacturer with several options available. The system should be secured and tensioned with a Hanger self-locking lock at the other end comprising of a single piece housing; the wedge inside the lock housing should be having serrated teeth & made up of sintered steel and springs used, if any, should be made up of stainless-steel. Once the grip is locked for safety purpose unlocking should only be done by using a separate setting key and should not be an integral part of the self-locking grip for safety purpose. Only wire and/or supports supplied and/or approved, shall be used with the system.

- Wire Hangers should have been independently tested by Lloyds Register. APAVE, TUV, CSA, Chiltern International fire, ADCAS, Intertek, ECA, and SMACNA, approved by ULC and CSA and comply with the requirements of DW/144 and BSRIA – wire Rope Suspension systems. Wire rope should be manufactured to BSEN 12385: 2002

- The contractor shall select the correct specification of wire hanger to use for supporting each particular service from table 1 below. Each size is designated with a maximum safe working load limit (which incorporates a 5:1 safety factor).

The correct specification of wire hanger required is determined using the following formula.

Weight per meter of object suspended (kg) X distance between suspension points (m) = weight loading per Hanger suspension point (kg).

Where the installed wire rope is not vertical then the working load limit shall be reduced in accordance with the recommendations give in the manufacturer’s handbook.

The contractor shall select the correct length of wire rope required to support the service. Lengths from 1-10m lengths. Specials can be made, check with manufacturer. No in–line joints should be made in the rope.

Table. 1

The standard range of Hanger Kits should contain galvanized high tensile steel wire rope or stainless steel wire rope as per the application, the minimum specification is as above and should be manufactured to BS 302 (1987), BSEN12385. Comply with manufacturer's load ratings and recommended installation procedures. Note the testing is done to the minimum breaking load of the wire thus giving a minimum safety factor of 5:1.

2.	Mechanical Supports – Wire Hanger Supports are suitable for: Water Pipes, Drainage Pipes, Gas Pipes, Refrigeration Pipes, Condensation Water Pipes.

    - Piping Supports: Rigid supports may be used in conjunction with wire hangers to assist with alignment of services as per the Schedule below. These can be at 30m intervals or so depending on the run of the service. Rigid support must also be used in conjunction with wire hangers with pipework at each change of direction or connection. For insulated pipe, provide protective sleeve to protect the entire circumference of the pipe insulation. Stainless Steel Supports should be available for food, chemical and High Corrosion areas near coastlines.

    - Any other wire hanging arrangement solution can be used based on manufacturer’s recommendation on site conditions after prior approval. Support piping in accordance with below Schedule at the end of this Section.

Refer to manufacturers catalogue and installation guide for further technical information. Comply with manufacturer's load ratings and recommended installation procedures. All supporting system to be provided by same manufacturer.

    - Pipe Hanger Schedule

Rigid Supports for pipes to be used in conjunction with wire supports:

| PIPE SIZE (mm) | PIPE SUPPORT |  |
| --- | --- | --- |
| UP TO 50 Ø | 40×40×6 M.S ANGLE |  |
| 80Ø TO 100Ø | 50×50×6 M.S ANGLE |  |
| PIPE SIZE (mm) | HORIZONTAL SUPPORT | VERTICAL SUPPORT |
| 125Ø TO 200Ø | 75×40 M.S CHANNEL | 50×50×6 M.S ANGLE |
| 250Ø TO 300Ø | 100×50 M.S CHANNEL | 75×40 M.S CHANNEL |
| 300Ø TO 400Ø | 150×75 M.S CHANNEL | 100×50 M.S CHANNEL |
| 450Ø TO 600Ø | 200×75 M.S CHANNEL | 200×75 M.S CHANNEL |

d.	Vertical pipes passing through floors shall be plumb and parallel to wall. Pipes shall be supported on alternate floor. MS cleats shall be wleded on pipes and rest on MS channel placed on the floor with 15 mm thick resistoflex pads between the cleat and channel. U clamps with resistoflex sheet shall be provided to keep the pipe in position.

e.	Bull heading in water/refrigerant piping shall be avoided.

f.	Pipe sleeves atleast 3 mm thick, 50 mm / 100 mm larger in diameter   than   condenser   /   chilled   water   pipes  respectively  shall  be  provided  wherever  pipes   pass through  retaining wall  and slab. Annular space shall  be  filled with fibreglass and finished with retainer rings welded on the ends of the sleeve.

g.	Wherever pipes pass through the brick or masonry / slab openings, the gaps shall be sealed with fire sealant such as fire barrier caulks.

h.	Insulated  piping shall be supported in such a manner  as not  to  put undue pressure on the  insulation.  20  gage metal sheet shall be provided between the insulation  and the clamp, saddle or roller, extending atleast 15 cm on both sides of the clamp, saddles or roller.

j.	All  piping work shall be carried out in a  workmen  like manner,  causing  minimum  disturbance  to  the  existing services,  buildings  and  structure.  The  entire piping  work  shall be organized,  in  consultation  with other  agencies  work, so that laying of  pipes,  supports, and pressure testing for each area shall be carried out in one stretch.

k.	Cut-outs  in the floor slabs for installing  the  various pipes  are  indicated in the Drawings.  Contractor  shall carefully examine the cut-outs provided and clearly point out where the cut-outs shown in the Drawings  do not meet with the requirements.

l.	The Contractor shall make sure that the clamps, brackets, clamp saddles and hangers provided for pipe supports  are adequate. Piping layout shall take due care for expansion and  contraction  in pipes and include  expansion  joints  where required.

m.	All pipes shall be accurately cut to the required size in accordance  with  relevant BIS Codes, edges bevelled and burrs  removed  before laying. Open ends  of  the  piping shall  be  closed  as  the pipe  is  installed  to  avoid entrance of foreign matter. Where reducers are to be made in horizontal runs, eccentric reducers shall be used  for the   piping  to  drain  freely.  In   other   locations, concentric reducers may be used.

n.	Flanged  inspection pieces 1.5 meters long,  with  bolted flanges  on both ends, shall be provided no more than  30 meters   centres, or where-ever  shown   in   Approved-for-Construction shop drawings, to facilitate future cleaning of all welded pipes.

o.	All  buried pipes shall be cleaned and coated  with  zinc chromate  primer  and bitumen paint,  and placed on concrete blocks with PUF  saddles dipped in bitumen at every   2 meters and wrapped  with three  layers  of fibre glass tissue, each layer  laid  in bitumen.

p.	Insulated  buried pipes shall be cleaned, derusted,  then coated  with Zinc chromate primer and placed on concrete blocks with PUF  saddles dipped in bitumen at every   2 meters. Insulation  shall  be applied as per the section “Insulation”, wrapped with  GI wire and covered with polyethylene sheet. Two coats (each 6  mm  thick)  of cement plaster shall  be  applied  over chicken  wire mesh lath. Buried insulated pipes shall be water-proofed using  coat of Shalibond, or approved adhesive, over  the plastered  surface; wrapping one layer of  fibre glass  RP tissue  and one layer of roofing tarfelt with  sufficient overlaps,  set  and  sealed with the  adhesive,  held  in position by 16 gage G.I wire tied at 15 cm intervals.

q.	Auto purge valves shall be provided at all highest points in the  piping system for venting air. Air valves shall be 15 mm pipe size with screwed joints.

Discharge  from the air valves shall be piped through  an equal  sized mild steel or galvanized steel pipe  to  the nearest  drain  or  sump. These pipes  shall  be  pitched towards drain points.

3	PRE-INSULATED PIPES

Pre insulated pipes, as called for in Technical Specification shall be sourced from the factory in length of minimum 6m. Metered dose of Polyurethane foam shall be injected in annular space between pipe OD and outer jacket to achieve average density of 36 Kg/m3.  After expanding, homogenous foam shall be formed between the cavity with no air gaps. Suitability of temperature range shall be from (-) 200C to 1200C.

Outer jacket shall be of  AL as indicated in Technical Specification.

4	PRESSURE GAGES AND THERMOMETERS

a.	Pressure  gages  as specified  under  section  “Automatic Controls  and  Instruments”  shall  be  provided  at suction and at discharge of each pump, at chilled water supply  and return  at  each air  handling  unit,  at  each chillers  and    condenser,  and as  shown on the approved Drawings  and  technical specifications. Care shall be taken  to  protect pressure gages during testing. Pressure gage sockets on insulated pipes and accessories shall be extended upto insulation to avoid damage of insulation for replacement of gages.

b.	Thermometers  as specified  under  section  “Automatic Controls  and Instruments” shall  be provided at chilled water supply and return  at each air  handling  unit, at each chiller and condenser, and as shown on Drawings and included in Technical Specification.

c.	Thermometers on CHW lines shall be with long stem. Thermometer socket shall be extended upto insulation thickness so that the thermometer shall be removable without damaging the insulation.

5	TESTING

a.	During construction , the contractor shall properly cap all lines, so as to prevent the entrance of sand, dirt, etc. Each system of piping shall be flushed thoroughly after completion (for the purpose of removing dirt, grit, sand etc. from the piping and fittings) for as long a time as is required to thoroughly clean the system.

|  | b. All piping shall be tested to hydrostatic test pressure of atleast two times the maximum operating pressure, but not less than the pressure mentioned in the SPECIFICATION for a period of not less than 24 hours. All leaks and defects in joints revealed during the testing shall be rectified, retested and gotten approved |
| --- | --- |

c.	Piping  repaired  subsequent to the above  pressure  test shall be re-tested in the same manner.

d.	Piping may be tested in sections and such sections  shall be securely capped, then re-tested for the entire system.

e.	The Contractor shall give sufficient notice to all  other agencies  at site, of his intention to test a  section  or sections of piping and all testing shall be witnessed and recorded by Owner/PMC-in-charge

f.	The contractors shall provide temporary pipe connections to initially by-pass condenser/chiller and circulate water through condenser/chilled water pipe lines for minimum 8 hours. Water should be drained out from the lowest point. The temporary lines shall be removed and blanked with dead flanges. Pot strainers and Y strainers shall be cleaned and fresh water filled in the circuits.

g.	The  Contractor  shall make sure  that  proper  noiseless circulation  of fluid is achieved through all  coils  and other heat exchange equipment in the system concerned. If proper  circulation  is  not achieved due  to  air  bound connection,  the Contractor shall rectify  the  defective connections. He shall bear all expenses for carrying  out the above rectifications including the tearing up and re-finishing of floors and walls if required.

h.	After  the piping has been installed, tested and run  for atleast  three  days  of eight hours  each,  all  insulated exposed piping  in  plant  room  shall  be  given  two finish coats, 3 mils each of approved colour,  conforming to relevant BIS Codes. The direction of flow of fluid  in the pipes shall be visibly marked with identifying arrows. For painting of insulated and clad pipes refer to Insulation section.

j.	After testing, all systems shall be chemically cleaned. Chemical cleaning shall be carried out in 3 stages. In first stage biological cleaning shall be done to remove algae, bacteria, SRB etc which produces slimes. Second stage is pre-cleaning in which loose rust, oil, and debris are removed. Chemical addition and hold up time shall be as per chemical supply agencies recommendations. Third stage is passivation, in which chemicals will be added and passivation film will be formed over inside surfaces of piping system. Type of chemical used and quantity of the same along with detailed method statement shall be submitted by contractor before starting this activity.

Before handover Owner/PMC-in-charge shall be provided with certificate of cleaning of pipe systems, signed by the  contractor.

k.  	The  Contractor  shall  provide  all  materials,   tools, equipment,  instruments, services and labour required  to perform  the  test  and to remove  water  resulting  from cleaning and after testing.

6	BALANCING

a.	After  completion of the installation, all  water  system shall  be  adjusted  and balanced to  deliver  the  water quantities as specified, quoted, or as directed.

b.	All balancing valves, Automatic  control valves and two-way diverting  valves shall  be  set  for  full flow  condition  during  balancing  procedure.  Each water circuit shall be adjusted thru balancing valves provided for this purpose; these shall be  permanently marked  after balancing is completed, so that they can  be restored to their correct positions, if disturbed.

c.	Complete  certified balancing report shall  be  submitted for  evaluation and approval by Owner/PMC-in-charge. Upon approval, four  copies of  the balancing report shall be submitted with  the  as-installed drawings and completion documents.

7	PIPE RISER SPECIFICATION

All vertical risers subjected to thermal expansion and / or contraction shall be supported by spring isolators and central anchors designed to insure loading within design limits at structural support points.  The design must include the initial load, initial deflection, change in deflection, final load and change in load at all spring support locations.  The anchors shall be capable of holding an upward force equal to the water weight when the system is drained.  If one level cannot accommodate this force, anchors can be located on 2 or 3 adjacent floors.

8	VALVE IDENTIFICATION

Provide 30 mm dia brass valve tag, with embossed letters and number for each valve and attach the tag to valve handle by “S” hook or by suitable means. Contractor shall provide valve tag schedule and valve chart for each piping system, consisting of schematic drawing of piping layout, along with a valve list, showing and identifying each valve by number, service and location and describing its function.

The contractor shall frame under glass in the airconditioning plant room or as directed by Owner/PMC-in-charge two copies of valve chart. Two additional unmounted copies shall be supplied to the Owner/PMC-in-charge.

Tags shall correspond with the valve schedule and record drawings. In back of house areas, where ceilings are installed and the valve or valve tag is not visible, a self adhering tag with the valve number shall be installed on the wall or directly under the ceiling.  For public area ceiling valves, these tags are to be installed in the service corridor, leading to the public areas.

- Motorized valves

- Ball  and  butterfly  valves  conforming  to  the following  specifications shall be provided as  shown  on Drawings :

-------------------------------------------------------------------------------------------------------

Size                 	Construction          	Ends    	Type			-------------------------------------------------------------------------------------------------------

15 to 25 mm          	Bronze 		Screwed	Ball

ASTM B62

32 mm and over     	Body Cast iron,    	Wafer		Butterfly

Type  and requirements shall be as indicated in technical specifications and approved drwings.  Valves shall have  non-rising  spindles  unless  specified  otherwise and shall be suitable for PN 16 rating. Butterfly valve should be of wafer type long neck construction single stem design with centre lugs to ensure proper alignment of pipe flanges. Mount valve onto flanges only after flanges have been welded to pipes using a tool piece and cooled down to room temperature to prevent damage to resilient seat. The rubber liner should be fully supported by the valve flanges. Appropriate dimensions and thickness of Flanges and Bolts, as per the Flange Tables ANSI B16.5 (#150 class), should be used. The flanges should be properly aligned with each other so that bolts are exactly perpendicular to the flanges.Evenly tighten the flange bolts to secure the valves. Counter flanges with nut-bolts and gaskets shall be provided by valve manufacturer.

Butterfly valves shall perform  the function of isolating valves and shall be suitable for PN16 rating.  Butterfly valves shall have Epoxy Coated cast iron body with Integrally moulded EPDM liner of replaceable type. The liner shall be integrally moulded on hard backup ring and shall be suitable for PN16 rating unless specified otherwise. All butterfly valves shall be provided  with  locking devices. Valves 250 mm  and above dia shall be gear driven.

- Automatic balancing valves shall automatically control flow rates with + 5% accuracy.  Valve control mechanism shall consist of a stainless steel cartridge with a ported cup and coil / helical spring to avoid corrosion.  Four operating ranges shall be available with the minimum range requiring less than 14 kPa to actuate the mechanism.  Manufacturer shall provide independent laboratory tests verifying assurance of performance.

- Balancing cum control valves shall be sized based on flow rates and pressure drops across cooling coil.

- Manual double regulating balancing valves shall be provided at chiller,  condenser, various tapp-offs and  each AHU  outlet line as indicated in Technical Specification.  These valves shall  have  built-in pressure-drop measuring facility to compute  flow   rate across  the valve. The test cocks shall be long  enough to  protrude out of  pipe insulation.  To enable accurate and practical operation, measurement of flow and differential pressure shall be made with a computerised balancing instrument which shall enable the operator to read the flow directly without the use of diagrams or tables.  In addition to measuring flowrate, differential pressure and temperature, computerised balancing instrument shall have a computer programme to provide the following functions:

i.	To balance the HVAC installation and calculate the necessary valve settings, based on system measurements.

ii.	To store the results of balancing.

iii.	To log measured values from a valve (differential pressure, flowrate or temperature).

iv.	To printout saved data in computerised measurement protocol (CMP) consisting of :

-	Name and size of Balancing Valve (BV)

-	Presetting position of BV

-	P at BV

-	Flow at BV

-	Design Flow

- The   supply   of flanges shall form part of piping (not separately identified in Technical Specification) and shall also include supply of bolts, washers,  nuts and  suitable asbestos fibre / rubber  insertion  gaskets (minimum   3 mm thick). Flanges shall be as per ANSI B16.1 class 150#.

- All ball valves and ball valves with Y strainer shall be bronze forged body construction with  chrome plated bronze ball and handle of stainless steel constructions. These are separately identified in Technical Specification.

- Non  return  valves  shall  be  dual  plate  check  valve provided as shown on the Drawings, and identified in Technical Specification conforming to relevant Codes and in accordance with the following Specifications :

-----------------------------------------------------------------------------------------------------------

Size                 		Construction                			Ends

-----------------------------------------------------------------------------------------------------------

40 to 300 mm       	Body: Grey Cast iron			Flanged

(Epoxy Coated),

CI IS 210 Gr. FG 260

Plates: CF-8 (SS-304),

Hinge/Stop Pin: SS-410

Spring(s): SS-316.

Seal: EPDM

350 mm to 500 mm   	Body: Grey Cast iron			Flanged

(Epoxy Coated),

CI IS 210 Gr. FG 260

Plates: SS-409.

Hinge/Stop Pin: SS-410

Spring(s): SS-316.

Seal: EPDM

The  spring  and hinge/stop pin shall be SS304  and  bearing PTFE material. Valves shall be PN 16 rating.

- Strainers shall be ‘Y’ type or Pot Strainer suitable for PN 16 rating as shown on drawings and included in SPECIFICATION.  ‘Y’ Strainer shall be fabricated out of MS ‘C’ class pipe two sizes higher than that of Strainer pipe size.  Flanges as per ANSI B16.5 (#150 class)shall be provided at inlet and outlet connectors.  The body shall be hot dip galvanized.  Permanent magnet shall be provided in the body of the Strainer to arrest MS particles. Filter element shall be of non magnetic 20 gage SS sheet with 3 mm perforation. Cartridge having five different type of filters made out of SS 304 with different mesh sizes shall be provided. These will be replaced so as to get good quality of water in system during commissioning. Strainers shall be provided at inlet of each Air Handling Unit and Pump as shown in drawings and included in SOQ.

Pot Strainers body shall be fabricated out of MS plate IS 226.  Thickness of sheet shall be as per size of the strainer chamfered pipes with flanges shall be provided at inlet /outlet connections of the strainer.  The tangential entry of water shall create a centrifugal action and due to velocity shall separate sediments  and deposit on the inner surface of Filter Element and at bottom of the Strainer.  Butterfly valves shall be provided at inlet / outlet connections as shown in drawing and included in SPECIFICATION.  The strainer body shall have two separate chambers properly sealed to avoid mixing of filtered and unfiltered water.  A powerful magnet shall be provided in the body to arrest MS particles.  Filter element of Pot Strainer shall be of non magnetic 18 gage SS sheet properly reinforced to avoid damage of the element.  A cone with sufficiently large drain pipe with butterfly valve shall be provided at the bottom chamber to flush-out foreign particles.  This arrangement shall avoid frequent opening of Pot Strainer for cleaning of filter element.  Gage connection shall be provided at inlet and outlet connection.

Pot strainers shall be provided with automatic backwash system if called for in SOQ. This shall be with heavy duty reduction gear motor provided at top of upper lid. During backwash, motorised drain valve shall be opened along with vent cock. Power supply cabling with tray shall be included in cost of pot strainer. Entire operation shall be through BAS.

A set of MS flanges with tongue and groove arrangement and neoprene rubber gasket shall be provided on the top cover and Pot Strainer flange with sufficient bolts and nuts to make the joint water light.  Bearing loaded tope cover lifting and swinging arrangement shall be provided.  The Pot strainer body shall be properly de-rusted and epoxy coated from inside and outside.  Manufacturers Test Certificate shall be provided with each Pot Strainer.

Size of various Pot Strainer, Filter Element and Thickness of MS sheet shall be as under:

-------------------------------------------------------------------------------------------------------

Pipe size    Pot Dia        Pot HT       Element Dia    	         Element HT    MS Plate Thickness

(mm)           (mm)            (mm)              (mm)              	  (mm)	          (mm)

---------------------------------------------------------------------------------------------------------------

50              300        	  400        	  200            	240		       6

80              350        	  450        	  250            	250		       6

100              450        	  500        	  300            	280		       6

125              500        	  600        	  330            	340		       8

150              540        	  700        	  360            	390		       8

200              610        	  815        	  400            	470		       8

250              800        	  955        	  550            	510		       8

300            1000       	1105        	  750            	580		       8

350            1190       	1300        	  895            	678                       12

400            1350       	1500        	1020            	785		      12

450            1518       	1700        	1060            	890                       12

500            1690       	1800        	1100            	900		     12

600            2000       	2200        	1500          	1160		     12

Each Port strainer shall be provided with a Test Certificate.

- All  chilled water piping & fittings, chilled water pumps, expansion tank and Air separator shall be  pressure  tested, painted and then insulated as described under  the section “Insulation”.

- Grooved coupling : Grooved coupling shall have 3 main parts viz. Housing, Gasket and bolting arrangement. Housing shall be made out of ASTM-A 536 Grade 65-45-12. The housing key shall engage into the grooves around the full pipe circumference, securing the pipe ends together with positive grip. Housing shall be designed to provide optimum  combination of pressure, stress relief and end load conditions while maintaining reasonable weight. Gasket shall be of high sealing efficiency and shall be able to withstand upto (-) 0.35 Bar pressure. Bolt shall confirm to ASTM A183, while nut shall confirm to ASTM A194. Nut-bolt shall be electro-galvanized.

- PRESSURE INDEPENDENT BALANCING CUM CONTROL VALVES

Each Air Handling Unit / Fan Coil Unit shall be provided with 2/3Way Pressure Independent Balancing Cum Control Valve with Integrated in a single Body with Globe Type in Construction as indicated in SPECIFICATION.

Control - Valve should be equipped with electronic modulating actuator which can accept either 4(0)-20 mA / 2(0)-10 V DC signals. Operating voltage for actuator shall be 24V AC. Delta p controller should ensure 100% valve authority at all loads (part load Actuator shall be able to work against maximum closing pressure of 6 Bar at full load). With feedback signal to Control system. 230/24V transformer shall be included.

Balancing – Each Valve should have steeples adjustable maximum flow limitation as per the designed flow rate of coils. Balancing should be done only in Valve not in actuator so that at any given condition of failure balancing is not lost and easily accessible.

All Valve actuator shall be microprocessor based with self calibrating feature.

Valve should be of linear control characteristics with stepless characteristics.

- VALVE SPECIFICATIONS

| Discription | For 15 to 32 mm | For 40 to 150 mm |
| --- | --- | --- |
| Diff Pressure (P1-P3) | 16 To 400 kPa | 35 To 600 kPa |
| Media Temperature | +1 ° to 110 °C, | -10 ° to 120 °C, |
| Body Material | Brass | Grey iron/Ductile iron |
| Test Ports | Needle measuring nipple | Needle measuring nipple |
| Shut off Leakage | Max. 0.05% of Kvs | Max. 0.05% of Kvs |
| Stem Seals | EPDM | EPDM |
| Maximum Close Off Pr | Minimum Should be 400 kPaD, | 600 kPaD |
| Pressure rating | PN16 or above | PN16 or above |

        - ACTUATOR SPECIFICATIONS FOR ALL SIZES

Supply Voltage		: 24V AC (230/24 Transformer shall be included)

Power Consumption		: 10V AC Max.

Frequency			: 50 HZ

Control Input			: 2-10V DC,  4-20mA, 3-point Selection.

Position Output		: 2-10V DC 4-20mA

Body Housing Insulation	: Non Corrosive - IP 40 or above

Valve Body and Characteristics

- Pressure Controller Device should maintain the Pressure, irrespective of fluctuations in the system with the help of a self adjusting diaphragm.

- Control valve shall accurately control the flow, with help of  Modulating Actuator

- All Valve Sizes should have Testing Ports for verifying the flow with respect to the Differential Pressure.

Valve Actuator and Housing

1.	Control/Dip Switch Setting should be easy to access for doing the balancing at site.

2.	The valve should be mounted with the actuator above the valve to prevent condensation water leaking into the actuator.

Valve Flow Balancing

- Balancing & Control: Balancing should be accomplished by the Diaphragm and Control should be taken care by Actuator receiving signals from Room Thermostats or BMS.

- Manual Override facility shall be provided to either open or close the valve.

- Flow Setting Balancing  (Commissioning) for the Valves should be simple and not require measuring devices.

- Proper operation of the valve should not be dependent on additional operations like de-airing of the valve or flushing procedures

# C.16	DUCTING WORKS, SUPPLY & RETURN AIR DIFFUSERS

# A.	 AIR DISTRIBUTION - (FOR DUCTS FABRICATED IN FACTORY AS PER “SMACNA”

# STANDARDS)

1	SCOPE

The scope of this section comprises design, supply fabrication, installation and testing of all sheet metal / aluminum ducts, supply, installation, testing and balancing of all grilles, registers and diffusers. All to be in accordance with these specifications and the general arrangement as per approved Drawings.

2	DUCT MATERIALS

2.1 	RAW MATERIALS

Galvanizing shall be Class VII – light coating of zinc, nominal 180gm/sq.m surface area and Lock Forming Quality prime material along with mill test certificates. In addition, if deemed necessary, samples of raw material, selected at random by Owner/PMC-in-charge shall be subject to approval and tested for thickness and zinc coating at contractor's expense.

2.2.	GAUGES, BRACING BY SIZE OF DUCTS

All ducts shall be factory fabricated from galvanized steel / aluminum of the following thickness, as indicated as below:

2.2.1	For Ducts with external SP upto 250 Pa (ESP upto 25mmWg)

|  | Rectangular Ducts G. S. | Pressure 250 Pa |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Duct Section Length 1.2 m (4 ft) |  |  |  |
|  | Maximum Duct Size | Gauge | Joint Type | Bracing Spacing |  |
|  | 1–500 mm | 26 | C&S Connector | Nil |  |
|  | 501 – 750 mm | 26 | C&S Connector | Nil |  |
|  | 751 – 900 mm | 26 | TDF Flange | Nil |  |
|  | 901 – 1200 mm | 24 | TDF Flange | Nil |  |
|  | 1201 – 1500 mm | 22 | TDF Flange | Nil |  |
|  | 1501 – 1800 mm | 22 | TDF Flange | JTR or ZEE BAR |  |
|  | 1801 – 2100 mm | 20 | TDF Flange | JTR or ZEE BAR |  |
|  | 2101 – above | 18 | TDF Flange | JTR or ZEE BAR |  |

*Distance of reinforcement/bracing from each joint.  Bracing material to be same as of material used for joining of duct sections.

FOR ALUMINUM DUCTS MATERIAL SHALL BE ONE COMMERCIAL GAUGE HIGHER WITH 22 G AS MINIMUM

2.3	For Round Ducts

| Duct diameter mm | Upto 50 mm Wg static pressure (+ve) |  | 51 – 250 mm Wg static pressure (+ve) |  | Upto 50 mm Wg static pressure (-ve) |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Spiral seam gauge | Longitudinal seam gauge | Spiral seam gauge | Longitudinal seam gauge | Spiral seam gauge | Longitudinal seam gauge |
| Upto 650 | 26 | 24 | 24 | 22 | 24 | 22 |
| 651-900 | 24 | 22 | 22 | 20 | 22 | 20 |
| 901 – 1250 | 22 | 20 | 20 | 20 | 20 | 18 |
| 1251 – 1500 | 20 | 18 | 18 | 18 | 18 | 16 |
| 1501 – 2100 | 18 | 16 | 18 | 16 | 16 | 14 |

3	FABRICATION STANDARDS & EQUIPMENT

All duct construction and installation shall be in accordance with SMACNA standards.  In addition, ducts shall be factory fabricated utilizing the following machines to provide the requisite quality of ducts.

- Coil (Sheet metal in Roll Form) lines to facilitate location of longitudinal seams at corners/folded edges only, for required duct rigidity and leakage free characteristics. No longitudinal seams permitted along any face side of the duct.

2.	All ducts, transformation pieces and fittings to be made on CNC profile cutter for requisite accuracy of dimensions, location and dimensions of notches at the folding lines.

3.	All edges to be machine treated using lockformers, flangers and rollers for turning up edges.

4.	Kitchen exhaust ducting shall be with 16 G MS welded construction. Suitable access doors shall be provided at every 3m. Provision shall be made for firefighting agency to install duct mounted sprinklers at every 3m. Generally, exhaust ducts shall have slope towards kitchen hood.

4	DUCT CONSTRUCTION

4.1 	All ducts shall be fabricated and installed in workmanlike manner, conforming to relevant SMACNA codes.

  - Ducts as per approved Drawings shall be acoustically lined and insulated from outside as described in the section “Insulation” and as indicated in Technical Specification. Duct dimensions shall be overall sheet metal dimensions inclusive of the acoustic lining where required and indicated in Technical Specification. The fabricated duct dimensions should be as per approved drawings and care should be taken to ensure that all connecting sections are dimensionally matched to avoid any gaps.

  - Ducts shall be straight and smooth on the inside with longitudinal seams shall be airtight and at corners only which shall be either Pittsburgh or snap button as per SMACNA practice, to ensure air tightness.

  - All ducts up to 75cms width within conditioned spaces shall have C&S connector.  The internal ends of slip joints shall be in the direction of airflow.  Care should be taken to ensure that Cleats are mounted on the longer side of the duct and Cleats on the shorter side. Ducts and accessories within ceiling spaces, visible from air-conditioned areas shall be provided with two coats of mat black finish paint.

  - Changes in dimensions and shape of ducts shall be gradual (between 1:4 and 1:7).  Air-turns (vanes) shall be installed in all bends and duct collars designed to permit the air to make the turn without appreciable turbulence.

  - Ducts shall be fabricated as per details shown on the approved drawings.  All ducts shall be rigid and shall be adequately supported and braced where required with standing seams, tees, or angles, of ample size to keep the ducts true to shape and to prevent buckling, vibration or breathing.

  - All sheet metal connection, partitions and plenums, required to confine the flow of air to and through the filters and fans, shall be constructed of 18 gauge GSS / 16gauge aluminum, thoroughly stiffened with 25mm x 25mm x 3mm galvanized steel angle braces and fitted with all necessary inspection doors as required, to give access to all parts of the apparatus.  Access doors shall be not less than 45cm x 45cm in size.

  - Plenums shall be shop/factory fabricated panel type and assembled at site.  Fixing of galvanized angle flanges on duct pieces shall be with rivets heads inside i.e. towards GS sheet and riveting shall be done from outside.

  - Self adhesive Neoprene rubber / UV resistant PVC foam lining 5mm nominal thickness instead of felt, shall be used between duct flanges and between duct supports in all ducting installation.

# B. AIR DISTRIBUTION - (FOR DUCTS FABRICATED AT SITE AS PER “BIS” STANDARD)

1	SCOPE

The scope of this section comprises design, supply fabrication installation and testing of all sheet metal / aluminium ducts, design, supply installation testing and balancing of all grilles registers and diffusers, (if required), in accordance with these specifications and the general arrangement shown on approved Drawings.

2	DUCT MATERIALS

All ducts shall be fabricated from galvanized steel sheets / aluminium  sheets of the following thickness as indicated  in Technical Specification.

G S S      ALUMINIUM

Rectangular ducts upto 75 cm          		24 gage       		22 gage

Rectangular ducts 76 to 150 cm

and all round ducts.                  		22 gage       		20 gage

Rectangular ducts 151 to 225 cm       	20 gage       		18 gage

Rectangular ducts greater than 225 cm 	18 gage       		16 gage

Sheet metal ducts shall be fabricated out of galvanized steel sheets. Fabrication of ducts shall be through well conditioned Triplex  lock former  or multiple lock formers, conforming to relevant  BIS Codes.  Sheets used shall be produced by Hot Dip Process and galvanizing  shall  be  Class  VII -  Light  Coating  of  zinc, Nominal 180 gm /Sq m surface area.

Samples of sheet  from  each  lot  selected  at  random  by Owner/PMC-in-charge site representative  shall be subject to approval  & gotten tested for  thickness and zinc coating at contractor’s  expenses.

3	All ducts shall be fabricated and installed in workmanlike manner, generally conforming to relevant BIS  Codes. Round exposed ducts shall be die-formed for achieving  perfect circle configuration.

3.1	a.	Ducts so identified on the approved Drawings shall be acoustically lined and insulated from outside as described in the section “Insulation” technical specifications.  Duct dimensions shown on approved Drawings shall be overall sheet metal dimensions inclusive of the acoustic lining where required and indicated in Technical Specification.

b.	Ducts shall be straight and smooth on the inside with neatly  finished  joints. All joints shall  be  made  air tight.

c.	All  exposed  ducts upto 60 cm width  within  conditioned spaces  shall have slip joints - or flanged  joints.  The internal  ends of slip  joints shall be in the  direction of air flow. Ducts and accessories within ceiling spaces, visible from air conditioned areas shall be provided with two coats of mat black finish paint.

d.	Changes  in  dimensions  and  shape  of  ducts  shall  be gradual.  Air-turns (Vanes)   shall be installed  in  all  bends and duct collars designed  to  permit  the air to make  the  turn  without appreciable turbulence.

e.	Ducts  shall  be  fabricated  as  per  details  shown  on approved Drawings.   All  ducts  shall  be  rigid  and  shall   be adequately  supported  and  braced  where  required  with standing  seams, tees, or angles, of ample size  to  keep the  ducts  true  to  shape  and  to  prevent   buckling, vibration or breathing.

f.  	All  sheet  metal  connection,  partitions  and   plenums required  to confine the flow of air to and  through  the filters and fans shall be constructed of 18 gage GSS / 16 gauge aluminium, thoroughly stiffened with 25 mm x 25  mm x 3 mm galvanized steel angle  braces and fitted with all necessary inspection doors as required, to give access to all parts of the apparatus. Doors shall be not less than 45 cm x 45 cm in size.

g.	Plenums shall be panel type and assembled at site. Fixing of galvanized angle  flanges on duct pieces shall be with rivets heads inside i.e. towards  G S sheet and riveting shall be done from outside.

h.	Self adhesive rubber lining minimum 5 mm thick instead of felt, shall be  used  between  duct flanges and between duct and duct supports  in all  ducting installation.

i.	Kitchen exhaust ducting shall be with 3mm thick MS sheet. Suitable access doors shall be provided at every 3m. Provision shall be made for fire fighting agency to install duct mounted sprinklers at every 3m. Generally exhaust ducts shall have slope towards kitchen hood.

# C. Pre-insulated ducts

Pre-Insulated Ducting shall be fabricated from 20 mm thickness air duct panel sheet having dimensions of 3000 (Length) mm by 1200 (Width) mm and produced and Sandwiched with Polyisocyanurate (PIR) first quality insulating Foam having 35 Kg / m3 density. The Ducting Sheet shall have Lacquered & Embossed Aluminium facing on both sides.

Insulating foam material shall be Expanded Rigid Polyisocyanurate foam having Closed cell content not less than 95%, CFC/ HCFC free, Non Toxic, Non-combustible, zero ozone depletion, Zero Global Warming Potential and Non ignitable.

Ducting panels shall comply with following or equivalent standards and manufacturer should produce M1 & F1 certification for Fire & Toxicity test results.

- BS 476: PART 6--Fire Propagation for Products

- BS 476: PART 7--- Surface Flame Spread (Class 1)

- Class O Fire Rating as per Building Regulation requirements.

- Thermal Conductivity Coefficient at 100C--0.022 W/m. K

- Smoke Opacity Index—less than 10

- Rigidity class: 200000 Nm m2/mm

- Water vapor permeability of laminations = 0

All required accessories; Connecting Flanges, Invisible Bayonet, Adhesive, Sealant, Duct Supports shall be part of ducting work for fabrication of the HVAC ducting in Square, rectangle, radius, offset construction etc., appropriate sizes of Aluminium flanges with self-adhesive good quality gasket shall be provided as a joinery or connection of duct pieces.

Excellent quality Silicon Neutral Sealant of Approved make along with fire rated PVC corners shall be used for sealing of all joints & corners.

Complete ducting shall be installed incorporating duct supports such as galvanized angles, threaded rods, self-adhesive brackets, Etc.

Panel Specifications: --

| Description | Internal Areas | External Areas of Building |
| --- | --- | --- |
| Dimensions of panel | 3000 x 1200 mm | 3000 x 1200 mm |
| Thickness of panel | 20 mm | 20/30 mm |
| Thickness of aluminium laminations | 60/60 microns | 60/200 microns |
| Density of the foam | 35 kg/m3 | 35 kg/m3 |
| Surface finish | Embossed/Embossed | Embossed/Embossed |
| Anti-rust lacquer | 2 gm/m2 both sides | 2 gm/m2both sides |

# D. INSTALLATION PRACTICE

All ducts shall be installed generally as per schematic drawings, and in strict accordance with approved shop drawings prepared by the Contractor and Technical Specifications:

- The Contractor shall provide and neatly erect all sheet metal work as may be required to carry out the intent of these Specifications and Drawings.  The work shall meet with the approval of Owner/PMC-in-charge in all its parts and details

- All necessary allowances and provisions shall be made by the Contractor for beams, pipes, or other obstructions in the building, whether or not the same are shown on the drawings.  Where necessary to avoid beams or other structural work, plumbing or other pipes, and conduits, the ducts shall be transformed, divided or curved to one side (the required area being maintained) all as per the site requirements.

- If a duct cannot be run as shown on the drawings, the contractor shall install the duct between the required points by any path available in accordance with other services and as per approval of Owner/PMC-in-charge.

- All ductwork shall be independently supported from building construction.  All horizontal ducts shall be rigidly and securely supported, in an approved manner, with hangers formed of galvanized steel wire ropes (as per support specification) and galvanized steel angle/channel or a pair of brackets, connected by galvanized steel wire hangers under ducts, rigid supports may be provided at certain interval if need be. The spacing between supports should be not greater than 2.4 meter. All vertical ductwork shall be supported by structural members on each floor slab. Duct supports may be through galvanized steel insert plates or Toggle end wire fixing left in slab at the time of slab casting. Galvanized steel cleat with a hole for passing the wire rope hanger shall be welded to the plates. Trapeze hanger formed of galvanized steel wire rope using Gripple shall be hung through these cleats.  Wherever use of metal insert plates is not feasible, duct support shall be through dash/anchor fastener driven into the concrete slab by electrically operated gun.  Wire rope supports shall hang through the cleats or wire rope threaded studs can be screwed into the anchor fasteners.

- Ducting over furred ceiling shall be supported from the slab above, or from beams after obtaining approval of Owner/PMC-in-charge.  In no case shall any duct be supported from false ceiling hangers or be permitted to rest on false ceiling.  All metal work in dead or furred down spaces shall be erected in time to occasion no delay to other contractor’s work in the building.

- Where ducts pass through brick or masonry openings, it shall be provided with 25mm thick TF quality expanded polystyrene around the duct and totally covered with fire barrier mortar for complete sealing.

- All ducts shall be totally free from vibration under all conditions of operation.  Whenever ductwork is connected to fans, air handling units or blower coil units that may cause vibration in the ducts, ducts shall be provided with a flexible connection, located at the unit discharge.  Flexible connections shall be constructed of fire retarding flexible heavy canvas sleeve at least 10cm long securely bonded and bolted on both sides.  Sleeve shall be made smooth and the connecting ductwork rigidly held by independent supports on both sides of the flexible connection.  The flexible connection shall be suitable for pressure at the point of installation.

- Duct shall not rest on false ceiling and shall be in level from bottom. Taper pieces shall taper from top.

# E. DAMPERS

a.	Dampers:  All duct dampers shall be opposed blade louver  dampers  of robust 16 G GSS construction and tight fitting. The design, method of  handling  and  control  shall  be  suitable  for  the location and service required.

b.	Dampers shall be provided with suitable links levers and quadrants as required for their proper operation. Control or setting device shall be made robust, easily  operable and  accessible  through  suitable access  door in  the duct.  Every  damper  shall have  an  indicating  device clearly showing the damper position at all times.

c.	Dampers  shall be placed in ducts at every branch  supply or  return air duct connection, whether or not  indicated on  the  Drawings,  for the  proper  volume  control  and balancing of the air distribution system.

e.	Pressure relief dampers: Pressure relief dampers shall be constructed with 18G Aluminum construction with parallel blade construction. Leafs shall be 100% air tight upon closure. Leafs shall be loaded with spring pressure of stiffness (k value) corresponding to set point pressure.

f.	Non return damper (Back draft damper) : Non return damper shall be constructed out of 16G GSS. Blades shall ensure 100% air leak proof performance on closure. Design shall ensure that no rattling noise is produced at design duty.

g.	Constant Volume Regulator shall be provided Constant volume regulators (KVR) shall be used to obtain constant air volume at a given pressure range.

The constant volume regulators (KVR) shall be of the circular type for high pressures and to be inserted into ductwork and suitable for vertical as well as horizontal mounting and it should be placed at a minimum distance of 3x the duct diameter from air supply grilles and minimum distance of 1x the duct diameter from air exhaust grilles

Constant volume regulator body, valve and piston shall be made out of flame retardant PVC, fire classification M1. They shall contain a self regulating PVC valve, piston, rubber strip for air tightness inside the duct and stainless steel calibrated spring and shall have preset air volume.

Constant volume regulator shall be made of PVC. The range covers an airflow range from 15 up to 1200 m³/h within a pressure range from 50 up to 600 Pa.

# F. FIRE & SMOKE DAMPERS

- All supply and return air ducts at AHU room crossings and at all floor crossings shall be provided with Motor operated Fire & smoke damper of at least 90 minutes rating as per UL555/1995 tested by CBRI, Roorkee. These shall be of multi-leaf type and provided with spring return actuator. Actuator shall have Form fit type of mounting, metal enclosure and guaranteed long life span.

- Fire damper blades and outer frames shall be of 16G galvanized steel construction fitted with atleast 400 mm long 18 gauge extended sleeves on both sides. The fire damper should be designed as per UL 555 standard that the fire damper should rest on wall and Actuator shall be fitted on extended sleeve and should operate Fire dampers with the help of linkages and extended shaft. The damper blade shall be pivoted on both ends using chrome plated spindles in self lubricated bronze bushes. Stop seals shall be provided on top and bottom of the damper, housing made of 16G galvanized sheet steel. For preventing smoke leakage metallic compression seals will be provided.

- The actuator shall be energized either upon receiving a signal from smoke detector installed in AHU room supply air duct / return air duct or temperature sensor. The fire damper shall also close upon sensing temperature rise in supply air ducts thru the electronic temperature sensor.

- Actuators shall be mounted on the sleeve by the damper supplier in his shop and shall furnish test certificate for satisfactory operation of each Motor Operated Damper in conjunction with its control panel. Control panel shall be wall mounted type.

- It shall be Contractor’s responsibility to co-ordinate with the Fire Alarm System services for correctly hooking up the Motor Operated Damper to Fire Detection / Fire Management System. All necessary materials for hooking up shall be supplied and installed by Contractor under close co-ordination with the fire protection system services.

- Contractor shall demonstrate the testing of all Dampers and its control panel after necessary hook up with the fire protection/fire management system is carried out by energizing all the smoke detectors with the help of smoke.

- Contractor shall provide Fire retardant cables wherever required for satisfactory operation and control of the Damper.

- Contractor shall strictly follow the instructions of the Damper Supplier or avail his services at site before carrying out testing at site.

- Fire/smoke damper shall be provided with factory fitted sleeves; however, access doors shall be provided in the ducts within AHU room in accordance with the manufacturer’s recommendations.

# G. SUPPLY AND RETURN AIR REGISTERS

Supply & Return air registers shall be of either steel or aluminium sections as specified in schematic drawings, technical specifications and approval from Owner/PMC-in-charge. Steel construction registers shall have primer Coat  finish whereas extruded aluminium registers shall be either Anodised or  Powder  Coated as per approval.  These registers shall have individually adjustable louvers both  horizontal and vertical. Supply air registers shall be provided with key operated opposed blade extruded aluminium volume control damper anodised in matt black shade.

The registers shall be suitable for fixing arrangement having concealed screws as  approved  by Owner/PMC-in-charge. Linear  continuous  supply cum return air  register  shall  be extruded aluminium construction with fixed horizontal bars at 15 Deg. inclination & flange on both sides only (none on top & bottom). The thickness of the fixed bar louvers shall be minimum 5.5 mm in front  and 3.8  mm  in  rear with rounded edges.  Flanges on the two sides shall  be 20 mm/30 mm wide as approved by Owner/PMC-in-charge. The grilles shall  be suitable  for  concealed fixing. Volume  control  dampers  of extruded  aluminium  anodised  in  black  colour   shall   be provided  in  supply  air duct collars. For fan coil units horizontal fixed bar grilles as described above shall be provided with flanges on four sides, and the core shall be  & suitable for clip fixing, permitting its removal without disturbing the flanges.

a.	All registers shall be selected in consultation with the Owner/PMC-in-charge. Different spaces shall require horizontal  or vertical face bars, and different width of margin frames.  These  shall  be procured only  after  obtaining  written approval from Architect for each type of register.

b.	All registers shall have a soft continuous rubber/foam gasket  between  the periphery of the  register  and  the surface on which it has to be mounted. The effective area of  the  registers for air flow shall not be less than 66  percent  of gross face area.

c.	Registers specified with individually adjustable bars shall have adjustable pattern as each grille  bar shall  be  pivotable to provide pattern with 0  to  +45 degree  horizontal  arc  and upto  30  degree  deflection downwards. Bars shall hold deflection settings under  all conditions  of velocity and pressure.

d.	Bar  longer  than 45 cm shall be reinforced  by  set-back vertical members of approved thickness.

e.	All volume control dampers shall be anodised aluminium in mat black shade.

# H. SUPPLY AND RETURN AIR DIFFUSERS/GRILLS

Supply and return air diffusers shall be as shown on the schematic drawings and Technical Specification and as per approval from Owner/PMC-in-charge. Mild steel diffusers/dampers shall be provided in Kitchen/Pantry and shall be factory coated with rust-resistant primer.  Aluminium diffusers shall be provided in the whole building and shall be powder coated & made from  extruded aluminium section.

a.  	Rectangular   Diffusers shall be extruded aluminium construction, square & rectangular diffusers with flush fixed pattern for different spaces. These shall be selected in consultation with the Owner/PMC-in-charge. These shall be procured only    after    obtaining    written    approval    from Owner/PMC-in-charge for each type of diffuser.

b.	Supply air diffusers shall be equipped with fixed air distribution grids, removable key-operated volume control dampers, and anti-smudge rings as required in specific applications, and as per approval from Owner/PMC-in-charge. All extruded aluminium diffusers shall be provided with removable central core and concealed key operation for volume control damper.

c.   	Linear    Diffuser    shall   be    extruded    aluminium construction  with  removable core, one or two  way  blow type. Supply air diffusers shall be provided with  volume control/ balancing dampers within the supply air  collar.  Diffusers  for  different  spaces shall  be  selected  in consultation  with  the Owner/PMC-in-charge, and  provided  as  per requirements  of  Technical Specification.  All  diffusers shall  have volume control dampers of extruded  aluminium construction powder coated in mat black shade.

d.	Slot Diffuser shall be extruded aluminium  construction multislot  type with air pattern controller  provided  in each  slot. Supply air diffusers shall be  provided  with Hit  &  Miss volume control dampers in each slot  of  the supply  air  diffusers. Diffusers  for  different  spaces shall be selected in consultation with the Owner/PMC-in-charge  and provided as per requirement of Technical Specification.

e.	Server Room shall be provided with floor grilles. Grilles shall be of nominal size of 600mm x 600mm and shall be fitted in floor tile of false floor. Grille shall be with dampers for flow control. Grill shall be heavy duty 16G Aluminium and shall take care of human traffic load.

# I. FIRE RATED DUCTWORK

Ducting for kitchen exhaust & fire evacuation shall be fire rated as per following specifications.

a.	All fire rated ductwork constructed for mechanical or dual ventilation/pressurization/basement car park/smoke extract systems and kitchen exhaust shall be fabricated from Lock Forming Quality grade prime Galvanized Steel Sheet, constructed to enhanced SMACNA American/DW144 European standard to either low, medium or high velocity/ pressure.

b.	Test requirement of fire rated ductwork should be tested to BS476: Part 24 [1987] and ISO 6944 providing required fire rating for Stability and Integrity.

c.	Stability: the ability of a duct, ductwork & the support system to remain intact & fulfil their intended function for a specified period of time, when tested to the requirements of BS476: Part 24 and ISO 6944.

d.	Integrity: the ability of a duct or ductwork to remain free of cracks, holes or openings out side the compartment in which the fire is present for a specified period of time, when tested to the requirements of BS476 Part 24 ISO 6944.

e.	Insulation: the ability of a duct or ductwork to maintain its separating function without developing temperatures on its external surface outside the compartment in which the fire is present, which exceeds, (i) 140OC as an average value above ambient & or, (ii) 180OC as maximum value above ambient at any point, when tested for a specified period of time to the requirements of BS476: Part 24 ISO 6944.

f.	Its important that the fire rated ductwork has a smooth internal surface in order to minimize the pressure loss within the fire rated ductwork system thereby reduce the power requirements.

g.	All fire rated ducts for Smoke Extract Duct shall have Stability / Integrity and Insulation for smoke temperatures up to 300OC upto 1.5 hrs, restriction of the duct due to twisting or buckling after the fire test shall not cause 25% or more reduction in cross sectional area proven by certification from an independent test house.

h.	Each duct shall have fire rated coating.  Fire rated coating compound used for construction of fire rated ductwork shall be protected with minimum 0.7mm to 1mm nominal thickness tested to properties as per the requirements of BS 476: 6 & 7, including non-combustibility Class O and fire propagation - Class 1 surface spread of flame & materials in accordance with Building Regulations.

i.	Fire duct to be tested / assessed to BS476: Part 24 for all sizes up to 25 meters x 3 meters cross-sectional area and fully certified to vertical and horizontal plane.

j.	Fire rated duct fabricated to Method 3 of BS 5588: Part 9, factory produced. The coating compound shall be applied either offsite or onsite on the ground, dried and cured.

k.	Fire duct expansion under fire conditions shall not exceed following,

- at    430OC an expansion of 0.006106mm per mm

- at    600OC an expansion of 0.00852mm per mm

- at  1100OC an expansion of 0.01562mm per mm.

# J. BRAIDED (WIRE) ROPE SUPPORT

- Steel Wire Rope Hangers& Supports:

Wire Hangers shall be used to suspend all static HVAC Air Distribution services.

Wire Hangers should consist of a pre-formed wire rope sling with a range of end fixings to fit various substrates and service fixings, these include a ferruled loop, permanently fixed threaded M6 (or M8, M10) stud, permanently fixed nipple end with toggle, at one end or hook or eyelet, cladding hook, barrel, wedge anchor, eyebolt anchor or any other end fixture type or size as per manufacturers recommendation and design. The end fixings and the wire must be of the same manufacturer with several options available. The system should be secured and tensioned with a Hanger self-locking lock at the other end comprising of a single piece housing; the wedge inside the lock housing should be having serrated teeth & made up of sintered steel and springs used, if any, should be made up of stainless-steel. Once the grip is locked for safety purpose unlocking should only be done by using a separate setting key and should not be an integral part of the self-locking grip for safety purpose. Only wire and/or supports supplied and/or approved, shall be used with the system.

- Wire Hangers should have been independently tested by -  Lloyds Register. APAVE, TUV, CSA, Chiltern International fire, ADCAS, Intertek, ECA, and SMACNA, approved by ULC and CSA and comply with the requirements of DW/144 and BSRIA – wire Rope Suspension systems. Wire rope should be manufactured to BSEN 12385: 2002.

- The contractor shall select the correct specification of wire hanger to use for supporting each particular service from table 1 below. Each size is designated with a maximum safe working load limit (which incorporates a 5:1 safety factor).

The correct specification of wire hanger required is determined using the following formula.

Weight per meter of object suspended (kg) X distance between suspension points (m) = weight loading per Hanger suspension point (kg).

Where the installed wire rope is not vertical then the working load limit shall be reduced in accordance with the recommendations give in the manufacturer’s handbook.

The contractor shall select the correct length of wire rope required to support the service. Lengths from 1-10m lengths. Specials can be made, check with manufacturer. No in–line joints should be made in the rope.

Table. 1

The standard range of Hanger Kits should contain galvanized high tensile steel wire rope or stainless-steel wire rope as per the application, the minimum specification is as above and should be manufactured to BS 302 (1987), BSEN12385. Comply with manufacturer's load ratings and recommended installation procedures. Note the testing is done to the minimum breaking load of the wire thus giving a minimum safety factor of 5: 1.

- HVAC Supports – Wire Hanger Supports are suitable for: Rectangular duct, Spiral Duct, Oval Duct, Fabric Duct, Plenum Boxes.

- Ducting Supports:

- All ductwork shall be independently supported from building construction.  All horizontal ducts shall be rigidly and securely supported, in an approved manner, with hangers formed of galvanized steel wire ropes and galvanized steel angle/channel or a pair of brackets, connected by galvanized steel wire hangers under ducts, rigid supports may be provided at certain interval if need be. The spacing between supports should be not greater than 2.4 meter.  All vertical ductwork shall be supported by structural/strut members on each floor slab. Duct supports may be through galvanized steel insert plates or Toggle end wire fixing left in slab at the time of slab casting. Galvanized steel cleat with a hole for passing the wire rope hanger shall be welded to the plates. Trapeze hanger formed of galvanized steel wire rope using hang fast shall be hung through these cleats.  Wherever use of metal insert plates is not feasible, duct support shall be through dash/anchor fastener driven into the concrete slab by electrically operated gun.  Wire rope supports shall hang through the cleats or wire rope threaded studs can be screwed into the anchor fasteners. In case of PEB structure Loop and Catenary system can be used based on the site conditions as per approved suspension system drawings.

    - All horizontal ducts shall be adequately secured and supported. In an approved manner, with trapeze Hangers formed of galvanized steel wire rope in a cradle support method (refer to typical drawings) under ducts at no greater than 3000mm centre, for 3001mm-above appropriate size anglealong with neoprene pad in between the duct & MS angle should be used with prior approval. All vertical duct work shall be supported by structural members on each floor slab. Duct support shall be through dash / anchor fastener driven into the concrete slab by electrically operated gun. Hanger wires shall then hang around the ducting. Rigid supports shall be used in conjunction with wire rope hangers to assist with alignment of services where recommended for by the manufacturer. Rigid support must also be used in conjunction with wire rope hangers with duct work at each change of direction or connection. Support ducting in accordance with table 2 at the end of this Section. Any other Wire hanging arrangement solution can be used based on manufacturer’s recommendation on site conditions after prior approval. In cases of Spiral ducting the wire can be wrapped directly around the ducting without the need for a spiral ducting clamp for sizes above 1100 a cradle support should be provided refer to manufacturer’s recommendations.

    - Ducting over furred ceiling shall be supported from the slab above or from beams after obtaining approval of Owner/PMC-in-charge. In no case shall any duct be supported from false ceiling Hangers or be permitted to rest on false ceiling. All metal work in dead or furred down spaces shall be erected in time to occasion no delay to other Contractor’s work in the building. All supports of pipe shall be taken from structural slab/wall by means of fastener.

- Catenary Supports:

    - Refer to manufacturer’s recommendations on Catenary supports with C-clip, special care should be taken with tensioning of the wire and angles at which the installation of services are made.

    - Stainless Steel Supports should be available for food, chemical and High Corrosion areas near   coastlines.

Refer to manufacturers catalogue and installation guide for further technical information. Comply with manufacturer's load ratings and recommended installation procedures.

Table 2: Duct Hanger Schedule

Notes: All supports are considered at 2400 mm interval in above table and may vary as per the design but should not be greater than 2400mm.

Rigid Supports:

If the MS angle at the bottom is required as per design it should be as per following table:

| Longer size of Duct | Type of Joints |
| --- | --- |
| Up to 750 | 25x25x3 mm L angle with M8 nuts & bolts |
| 751-1000 | 25x25x3 mm L angle with M8 nuts & bolts |
| 1001-1500 | 40x40x5 mm L angle with M8 nuts & bolts |
| 1501-2250 | 50x50x5 mm L angle with M10 nuts & bolts |
| 2251 & above | 50x50x6 mm L angle with M10 nuts & bolts |

All the supporting system should be supplied from same manufacturer.

# K. VAV Terminal boxes

VAV Terminal Boxes - General

All the VAV Terminals shall be Pressure Independent type with Direct Digital Controls to regulate the primary air flow rate between the scheduled minimum and maximum values to achieve the specified comfort level within acceptable noise criteria. A separation shall be made in Induction VAV Terminals and Standard VAV Terminals as detailed in the schedule.

The Induction VAV Terminals shall induce room air, without need of an assisting fan, and mix it with conditioned primary air, maintaining a near constant air volume to the room thus providing sufficient air movement necessary to maintain occupant comfort even in extreme load variations.

The VAV terminal shall have the controls, actuators and transformers, etc. pre-fitted, wired and calibrated at the factory and supplied with its appropriate digitally communicating thermostat. The supply of the VAV Terminals and the VAV controls, as well as the commissioning at the site, shall be done by the same specialist/local supplier.

VAV box shall be provided with terminal re-heater section if indicated in Technical Specification.

Construction of Standard Pressure Independent VAV Terminals

The casing shall be a double wall construction made from galvanized sheet steel (non spiral). Casing Leakage Rate shall be according to class II, VDI 3803/DIN 24 194. The insulation thickness shall be 25 mm. and the insulation material shall be fully enclosed by the metal casing. VAV Terminals with insulation materials in direct contact with the air flow will not be accepted.

The VAV Terminals shall have a low leakage, sandwich construction damper blade with SBR gasket and a solid aluminum damper shaft (diameter 12 mm.) with self lubricating Nylon bearings. The leakage shall be less than 2% of the nominal flow at 750 Pa. inlet static pressure. The duct sleeve connections at the inlet and outlet of the VAV Terminal shall be conform DIN 24 145 or DIN 24 146 respectively.

For large air volumes, Rectangular VAV Terminals shall be provided. These Rectangular VAV Terminals shall have a multi-leaf opposed blade damper with aluminum, aerofoil blade construction, width 50 mm. and external linkage. The damper spindle shall be made of steel (10 mm. diameter), rotating in self lubricating Nylon bearings. The VAV Terminal shall have 30 mm. flange connections at the inlet and outlet of the terminal.

Each VAV Terminal, Circular or Rectangular shall be factory fitted with a multipoint, averaging air flow sensor in the inlet of the terminal. This air flow sensor shall amplify the air pressure signal linearly with an amplification factor of at least 2.0. The air flow sensor shall contain not less than 2x12 sensing points, which shall be arranged in two perpendicular axis of sensing. The holes shall be arranged in such a way that each four points in a ring sense the air pressure across concentric circles of equal area in a round duct. The signal shall be averaged and measured from the center of the sensor. And the accuracy shall be within 2.5% even with irregular duct approach.

Construction of Induction VAV Terminals (Pressure Independent)

The casing shall be rectangular type made from galvanized sheet steel (thickness 1.25 mm.) with a circular inlet, two Induction openings at the sides of the terminal and a rectangular outlet. The duct sleeve connections at the inlet and outlet of the VAV Terminal shall be conform DIN 24 145 or DIN 24 146 respectively. The VAV Terminal shall have internal insulation (thickness 25 mm.), tested HF-1 (UL 94) flame test and erosion proof up to 50 m/s air velocity.

The terminals shall be fitted with a specially constructed jet-tronic damper to regulate the primary air flow between the scheduled minimum and maximum values. The same damper shall also generate and control the Induction effect through the acoustically lined induction chamber of the VAV Terminal. The damper shaft shall be solid aluminum (diameter 12 mm.), rotating in self lubricating Nylon bearings. The damper shall permit proper operation of the terminal over a range of 20 to 100% of maximum flow without the requirement of special VAV diffusers or assisting fans.

The Induction VAV Terminal shall be factory fitted with a multipoint, averaging air flow sensor in the inlet of the terminal. This air flow sensor shall amplify the air pressure signal linearly with an amplification factor of at least 2.0. The air flow sensor shall contain not less than 2x12 sensing points, which shall be arranged in two perpendicular axis of sensing. The holes shall be arranged in such a way that each four points in a ring sense the air pressure across concentric circles of equal area in a round duct. The signal shall be averaged and measured from the center of the sensor. And the accuracy shall be within 2.5% even with irregular duct approach.

# L. FLEXIBLE DUCT

Insulated flexible duct should be UL 181 CLASS I AIR DUCT LISTED AND LABELLED WITH NFPA 90A & 90B ANDSEAL OF AIR DIFFUSION COUNCIL with double lamination of tough polyester which encapsulates steel helix wire forms the air tight inner core , double layer core wrapped in a multiple thickness of fiberglass wool with R Value 4.2 , Green guard certification of fiberglass wool must.  , Reinforced and sheathed in a rugged and durable tridirectionally reinforced matlized polyester jacket.

Flexible duct connections should be made as per UL181 listing procedure with proper  flexible right forming brace connection allowing right connections for flexible duct into energy efficient . and Strapping the flexible duct connections with flexible duct strap ties.

M. TESTING AND BALANCING

After the installation of the entire air distribution system is completed in all respects, all ducts shall be tested for air leaks by visual inspection.

The entire air distribution system shall be balanced using an anemometer.  Measured air quantities at fan discharge and at various outlets shall be identical to or less/excess than 5 percent in excess of those specified and quoted.  Branch   duct adjustments shall be permanently marked after air balancing is completed so that these can be restored to their correct position if disturbed at any time.  Complete air balance report shall be submitted for scrutiny and approval, and four copies of the approved balance report shall be provided with completion documents.

# C.17	INSULATION

- SCOPE

The scope of this section comprises the design, supply and application of insulation conforming to these specifications.

- MATERIAL

- Insulation material shall be Closed Cell Microcellular Elastomeric Nitrile Rubber.

- The Density of Material shall be between 40 to 60 Kg/m3.

- Thermal conductivity of elastomeric nitrile rubber shall not exceed 0.036 W/mK at an average temperature of 0C.

- The insulation shall have fire performance such that it passes minimum fire rating Class 1 as per BS 476 Part 7 for surface spread of flame and also pass Fire Propagation requirement as per BS476 Part 6 to meet the Class ‘O’ Fire classification as per 1991 Building Regulations (England & Wales) and the Building Standards (Scotland) Regulations 1990.

- Water vapour permeability shall not exceed 0.024 Perm inch (2.48 x 10-14 Kg/m.s.Pa) i.e. Moisture Diffusion Resistance Factor or ‘µ’ value should be minimum 10,000.

- Material should have FM Global (Factory Mutual) USA approval for fire behavior.

- Insulation material shall have Ultra-Fresh® anti-microbial protection, which is EPA (Environmental Protection Agency), USA approved (or equivalent), as an integral part  of  insulation  that  cannot  be washed off or worn off as per ASTM G-21

- It shall give enhanced level of protection against harmful Microbes such as bacteria, mold, mildew and fungi

- Should also pass Smoke Toxicity of the product according to DIN 5510 Part 2 appendix 2

- Should have VOC emission Class A+ as per ISO 16000.

- Insulation products shall be free from CFC/HCFC, Formaldehyde, Dust & Fibres

- Material should have low temperature flexibility conforming to ASTM D 1056 -07

- Ozone resistance as per ASTM D 1171-99(07)

Thickness of the insulation shall be as specified for the individual application.

- DUCT INSULATION (INDOOR)

External thermal insulation shall be provided as follow:

The thickness of Nitrile rubber shall be as per approved drawing and as per technical specifications. Following procedure shall be adhered to:

- Duct surfaces shall be cleaned to remove all grease, oil, dirt, etc. prior to carrying out insulation work.

- Measurement of surface dimensions shall be taken properly to cut closed cell elastomeric rubbers sheets to size with sufficient allowance in dimension.

- Material shall be fitted under compression and no stretching of material shall be permitted.

- A thin film of Synthetic Rubber based adhesive shall be applied on the metal surface and then on the back of the insulating material sheet.

- When adhesive is tack dry, insulating material sheet shall be placed in position and pressed firmly to achieve a good bond. Also care should be taken to prevent the trapping of air bubbles between metal sheets and insulating material sheet.

- All duct flanges should be covered properly with a 150mm wide strip of insulation sheet after gaining uniform height by applying multiples layer of 75mm wide strip of insulation sheet from the both side of flanges.

- All longitudinal and transverse joints shall be sealed with adhesive tapes of 50mm (wide) x 3mm (thick).

- The adhesive shall be strictly as recommended by the manufacturer.

- The detailed Application specifications are as per the manufacturer’s application manual.

- INSTALLATION OF DUCTS EXPOSED DIRECTLY TO SUNLIGHT:

For installations exposed to sunlight specified thickness of insulation sheet with a factory applied black glass fabric covering of 200gsm ±5% should be installed with application procedure same as Indoor installation and apply two coats of epoxy paint/ Starbond or equivalent after giving 36 hours curing time for the adhesive apply manufacturer’s recommended UV/Mechanical Protection. No locally available separate glass fabric shall be allowed for UV protection treatment. Please refer the separate detailed guidelines on UV/Mechanical Protection.

- PIPING INSULATION

All chilled water, refrigerant and condensate drain pipe shall be insulated in the manner specified herein. An air gap of 50 mm shall be present between adjacent insulation surfaces carrying chilled water or refrigerant and also between the insulated surface and the wall to allow natural ventilation without affecting its external surface coefficient of heat transfer.  Before applying insulation, all pipes shall be brushed and cleaned. All Pipe surfaces shall be free from dirt, dust, mortar, grease, oil, etc. Thermal insulation shall be applied as follows or as specified in approved drawings and technical specifications.

Insulating material in tube form shall be sleeved on the pipes.

- On existing piping, slit opened tube of the insulating material (slit with a very sharp manufacturer’s recommended knife for straight line longitudinal cuts) shall be placed over the pipe and adhesive shall be applied as suggested by the manufacturer.

- Adhesive must be allowed to tack dry and then press surface firmly together starting from butt ends and working towards centre.

- Wherever flat sheets shall be used it shall be cut out in correct dimension. All longitudinal and transverse joints shall be sealed with of 50mm (wide) x 3mm  thick) adhesive tape The insulation shall be continuous over the entire run of piping, fittings and valves. Multiple layer of Insulation sheet wherever applicable should be applied to stagger all longitudinal & transversal joints.

- All valves, fittings, joints, strainers, etc. in chilled water piping shall be insulated to the same thickness as specified for the main run of piping and application shall be same as above. Valves bonnet, yokes and spindles shall be insulated in such a manner as not to cause damage to insulation when the valve is used or serviced.

- RECOMMENDED ADHESIVE

Type: Synthetic Rubber Adhesive

Colour: Beige/ Dark Brown

Drying Time: < 10 Hrs under ambient conditions

- PUMP INSULATION

Chilled water pump shall be insulated to the same thickness as the pipe to which they are connected and application shall be same as above. Care shall be taken to apply insulation in a manner as to allow the dismantling of pumps without damaging the insulation.

- SHELL INSULATION

The chiller shells shall be factory insulated in accordance with the manufacturer’s standards.

- COLD WATER AND EXPANSION TANK INSULATION

Cold water tank, and chilled water expansion tank shall be insulated as per manufacturer’s standard.

- PIPE SUPPORTS

All pipe supports shall be factory made as per specification.

- INSTALLATION EXPOSED DIRECTLY TO SUNLIGHT

For installations exposed to sunlight, after giving 36 hours curing time for the adhesive apply manufacturer’s recommended UV/Mechanical Protection. Please refer the separate detailed guidelines on UV/Mechanical Protection and choose the right product, as needed for specific requirement. For pipe diameter upto 80mm Black glass fabric UV protection tape should be used and for pipe diameter more than 80mm Insulation sheet with factory laminated black UV protection glass fabric of 200 gsm ± 10% IC Clad should be used. No site installation of locally available glass fabric shall be allowed for UV protection treatment.

Note: All thicknesses to be verified by the Contractor and calculations submitted for approval to the Owner/PMC-in-charge.

- THICKNESS SELECTION CHART FOR NITRILE RUBBER INSULATION

Design Basis: Condensation Control

Non Coastal Areas:

Outdoor / indoor design conditions: 30 deg. C & 82 % Rh

- Chilled Water Piping Line Temp 7 Deg C

| Pipe NB (mm) | Required Thickness |
| --- | --- |
| Up to 32 | 19mm |
| Up to 600 | 25mm |
| Chilled Water Tank | 25mm |

- Drain Piping: Line Temperature 15 Deg C

| Pipe NB (mm) | Required Thickness |
| --- | --- |
| Up to 50 | 13mm |
| Above 50 | 19mm |

- Refrigerant Piping: Line temp 3 deg c

| Pipe NB (mm) | Required thickness |
| --- | --- |
| Up to 50 | 25mm |
| Up to 100 | 32mm |

- Duct Insulation

|  | Required Thickness |
| --- | --- |
| S A Duct (Line Temp. 14 Deg. C)in Unconditioned Space | 19mm |
| S A & R A Duct in Conditioned space | 9mm |
| SA Duct exposed to weather | 19mm |
| RA Duct exposed to weather | 9mm |
| Acoustic Insulation( lining ) for ducts | 15mm |
| AHU wall / Room acoustic lining | 25mm |

- ACOUSTIC INSULATION

MATERIAL:

- Material shall be Owner/PMCed  Nitrile Rubber open cell foam

- The Random  Incidence Sound Absorption Coefficient  (RISAC);  tested  as per  ISO 354, shall be minimum as per enclosed chart

| Freq (Hz) | 125 | 250 | 500 | 1000 | 2000 | 4000 | NRC |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 10mm thick | 0.00 | 0.05 | 0.15 | 0.55 | 0.90 | 0.85 | 0.41 |
| 15mm thick | 0.05 | 0.10 | 0.25 | 0.75 | 0.95 | 0.85 | 0.51 |
| 20mm thick | 0.03 | 0.16 | 0.56 | 0.56 | 0.86 | 0.80 | 0.53 |
| 25mm thick | 0.06 | 0.23 | 0.80 | 1.20 | 1.01 | 1.06 | 0.81 |
| 30mm thick | 0.07 | 0.29 | 1.10 | 1.05 | 0.90 | 1.14 | 0.84 |

- The material shall be fibre free

- The density of the same shall be within 140-180 Kg/m3

- The material shall have a thermal conductivity not exceeding 0.047 W/m.K @ 20 Deg. C

- The  material  shall  withstand  maximum  surface  temperature  of  +850C  and  minimum surface temperature of -200C

- The material shall conform to Class 1 rating for surface spread of Flame in accordance to BS 476 Part 7 & UL 94 (HBF, HF 1 & HF 2) in accordance to UL 94, 1996.

- The insulation shall pass Air Erosion Resistance Test in accordance to ASTM Standard C 1071-05 (section 12.7), from an independent testing agency.

- The insulation should have built-in Anti-Microbial Protection, and should pass Fungi Resistance as per ASTM G21 & Bacterial resistance as per ASTM 2180.

Thickness of the material shall be as specified for the individual application. The insulation shall be installed as per manufacturer’s recommendation.

- DUCT ACOUSTIC LINING

Ducts as per approved Drawings shall  be provided with acoustic lining of Open Cell Acoustic Insulation material for a distance of minimum 8 meters (or 30% of the duct length whichever is more).

Installation Procedure

The inside surface for  the  ducts  shall  be  covered  with  adhesive recommended  by  the manufacturer. Cut Foamed sheets into required sizes apply adhesive on inside wall of duct as well as on the foam and stick it to the duct surface. At the starting point for the ducting from AHU put a flange and bend it towards the foam.

- The wall surface shall be cleaned and required surface preparation shall be done for applying adhesive.

- Rubber based contact adhesive recommended by the manufacturer shall be used.

- Foam sheets shall be cut to required size and a thin layer of adhesive shall be applied to both the surfaces; Insulation and inside duct.

- When it is tack dry, it is applied / stuck with enough pressure to the walls/ceiling. Minimum 5 fasteners with washer (of G.I Sheet 2.5-inch x 2.5 inch) / square meter, 4 at corners & 1 at centre shall be put immediately after sticking with the help of adhesive. The length of the fastener shall be minimum 75 mm.

- The acoustic lining of walls shall be terminated approximately 15cm above the finished floor to prevent damage to insulation due to accidental water logging in plant / AHU Rooms.

- INSULATION COVERING / CLADDING

15.1	UV / Mechanical Protection for Piping / Ducting / Equipments / Vessels

a.  Treated Woven Glass Cloth Covering (Factory Applied on Insulation sheets by Insulation Manufacturer)

Specification Clause:

For protection of Insulation material against mechanical impact, damage by ultra voilet radiations and Scratch etc. –Black colour / Metalic Silver colour (as per approval) treated woven glass fabric covering - shall be applied. It shall not have any fibre erosion. (For Indoor application only). No local separate glass fabric covering shall be allowed. Colour of covering shall be preferably black for its thermal advantages.

Technical Details:

Temperature Range: - 50°C to +105°C

Colour: Black

Area weight : 200 ± 10%  gm / m2

Application Notes:

The covering shall be cut to size according the circumference of the insulated pipe – please allow an additional 50mm for the overlap of the covering material. The Overlap shall be securely fixed using recommended Adhesive or a self adhesive covering is recommended for pipes below 80mm NB.

Spread thin film of recommended on the 50mm overlap and close the seam. When covering fittings, please consult the manufacturer’s Application Manual. All fittings have to be covered to the same standards as the covering of the pipe work. No additional vapor barrier is needed.

For outdoor application, apply manufacturer recommended mastic on all seams and joints.

- Metallic Flexible Polymeric Covering with UV resistant properties:

Specification Clause:

For protection against mechanical impact and UV attack metallic flexible polymeric barrier –- with a high resistance to Oil and Chemicals – should be applied.

Technical Details

Line temperature Range: 0°C to +105°C

Permeability to vapour : 0.052 g/m2/d conforming to DIN 53122

Weight : 388 gms/m2 (+/-5%)

Thickness : 300 microns (+/-5%)

Traction resistance as per ISO 527-3 : Longitudinal 175 N/15 mm Transverse 175N/15mm

Breaking strength ISO 527-3 : Longitudinal 35% Transverse 40%

Tear Strength according to ISO 527-3: Longitudinal 155 N/25mm Transverse 182 N/25mm

Resistance to bending according to ISO 53 864 : Longitudinal 90 N/mm2 Transverse 90 N/mm3

Dust & Fibre Free

Colour: Dull Aluminium metallic finish

Application Notes:

Flexible Metallic Polymeric covering (with or without adhesive) should be cut to size according the circumference of the insulated pipe – please allow an additional 50mm for the overlap of the Flexible Polymeric Covering material. The Overlap shall be securely fixed using manufacturer recommended Adhesive. All seam and joint details shall be over covered with adhesive tapes.

In case of AL Clad without adhesive spread thin film of Adhesive on the 50 mm overlap and the corresponding face to be adhered to and close the seam. For covering butt joints use AL Clad adhesive tapes. When covering fittings, please consult the manufacturer’s Application Manual. All fittings have to be covered to the same standards as the covering of the pipe work. No additional vapor barrier is needed.

For further guidance please consult manufacturer’s Application manual/ technical department for onsite application support.

- Flexible PVC UV Resistant covering:

PVC rigid self-rolling sheet with a smooth grey surface. The sheet sticks perfectly to all cylindrical pre-insulated surfaces. Lightness and ease of handling are some of the practical qualities of this self-extinguishing product that does not drip and protects the insulation, improving its overall appearance. To keep the characteristics of this product intact, it is advisable to stock the rolls, during cold weather, at room temperature for 24 hours before use.

USE: It is used as a protective covering and to improve the overall appearance of large and small cylindrical pipes insulated with elastomeric material, fibre-glass mattresses, mineral wool, polyurethane cupels and polystyrene.

Technical Details:

Base: 				: rigid PVC

Fire: 				: Homol. MI700C50CD100009

Colour				: standard light grey

Packaging			: Rolls

Sheet thickness		: 0.30 mm ÷ 0.35 mm

Temperature range		: from -25 °C to +70 °C

Thermal conductivity λ	: 0.16 W/(m•K)

Permeability to vapour μ	: 1.0 gm2 24h Pa

Application Notes:

Calculate the correct amount of sheet required leaving an overlap of a few centimeters for overlapping the joining borders. Wrap the sheet around the insulation Seal the borders with plastic rivets (see reference in the section components: fixing products”)

Please allow and 50mm overlap of the PVC Covering material. For further guidance please consult manufacturer’s Application manual/ technical department for on-site application support.

- Factory faced Aluminium foil flexible Covering:

Specification Clause:

Factory faced FSK (Foil Scrim Kraft) type or PE film with class O fire rating.

Technical Details:

This Foil should be UV resistant and should provide protection against mechanical damage to the insulation.  The foil should factory laminated on the insulation for sheets. It should have a Dull surface finish. Use of foil in areas exposed to weather not also recommended. Also please consult our technical department as thickness of insulation may go up with the use of foil due to change in the emissivity coefficient of the glossy surface.

Application Notes:

The sheets with Alu foil sheets, should be installed in similar manner to installation of regular sheets. All the joints shall be sealed using an Alu Foil Tapes.

Storage: Material should be stored under covered roof at room temperature upto 30 Deg C. It should not stored in exposed areas open to atmosphere.

15.2	Adhesive:

- Adhesive for Duct Application

The adhesive shall be specially formulated for the Duct insulation application and supplied by insulation manufacturer. The adhesive shall be rubber based, solvent based contact adhesive, free from benzene.

The adhesive shall be quick drying characteristics for tropical conditions and shall have service temperature of 0 0C to +85 0C.

The VOC content in the adhesive should be low.

Application Notes:

Be sure that the surfaces are clean and dry, and then spread K-414 homogeneously on both surfaces and let it dry for 5-10 min. Then join the two surfaces and press them properly for few seconds (5-10 sec) in order to get intimate contact.

The bonded pieces are immediately ready for further processes.

In case you wait time longer than open time before assembling, it is necessary to warm up a little bit the two surfaces in order to have them tacky again.

High room temperatures make open time longer, low room temperatures make it shorter.

On high porous surfaces, two coats of adhesive are sometime suggested

b.  Adhesive for Pipe Application

The adhesive shall be specially formulated for the Duct insulation application and supplied by insulation manufacturer. The adhesive shall be rubber based, solvent based contact adhesive, free from benzene.

The adhesive shall be quick drying characteristics for tropical conditions and shall have service temperature of 0 0C to +85 0C.

Application Notes:

Be sure that the surfaces are clean and dry, and then spread K-414 homogeneously on both surfaces and let it dry for 5-10 min. Then join the two surfaces and press them properly for few seconds (5-10 sec) in order to get intimate contact.

The bonded pieces are immediately ready for further processes.

In case you wait time longer than open time before assembling, it is necessary to warm up a little bit the two surfaces in order to have them tacky again.

High room temperatures make open time longer, low room temperatures make it shorter.

On high porous surfaces, two coats of adhesive are sometime suggested.

15.3	Factory made Elastomeric Nitrile Rubber Pipe Supports:

Specification Clause:

Insulated  pipe  support,  single  piece  with  self-adhesive  closure,  PUR/PIR  load  bearing Insert (Density 120 kg/m³) embedded in elastomeric nitrile rubber insulation with two outer metal shells made of aluminum sheet, which also acts as a vapour barrier  for  the PUR/PIR inserts.

Technical Details:

Temperature Range: - 45°C to +105°C

Compression resistance 1350 kPa

Moisture Resistance Factor μ: 7000

Thermal Conductivity at 0°C: 0.036 W/(m · K)

Colour: Black

15.4	Self Adhesive Joints Sealing Tapes:

Joints in the insulation work are most susceptible areas for Condensation. Effective care has to be taken to make the all the joints in the insulation are properly sealed.

All the insulation joints should be sealed using Joint sealing Self adhesive tapes recommended by manufacturer for the respective covering.

The tapes are as given below:

- Plain Nitrile tapes: 3mm thick x 50mm Width

- Alu Foil Tapes

- PVC Tapes

- AL Clad Tapes

- IC-Clad Tapes (Glass cloth tapes)

15.5	UV Resistant Paint:

Material shall be water-based paint for coverings on internal and external installations insulated with Nitrile materials. With its polymerized acrilic base, it does not pollute and does not give off odours, and is particularly recommended for all indoor uses. Quick drying, it offers excellent protection. Coats of white paint, spread over the layer, maintain their colour even in dark environments. The colours are resistant to light. It is advisable to paint the surface of the externally insulated pipe to protect them against harsh weather conditions and UV rays. For further protection it is advisable use a double layer of paint.

- SERVER ROOM FLOOR INSULATION

Floor of Server Roomshall be insulated with 9mm thick EPDM rubber insulation as per specifications. 750mm x 750mm grid shall be made on the floor. This grid shall be made from 25mm wide 22G GI  C-section. These C-sections shall be screwed to floor. Depth of screwing in to the floor shall not be more than 5mm. Sections of insulation shall be sticked to floor with self adhesive / adhesive solution as recommended by insulation manufacturer.

- SOUND ATTENUATORS

Attenuators  shall be installed in ducts in  accordance  with requirements  of  approved drawings  and technical specifications.

Noise levels within conditioned spaces shall be not greater than those set out in schedule below :

a.	Noise Level Design Criteria

-------------------------------------------------------------------------------------------------

S.No. 	Area                                       		Acceptable Noise Levels (NC)

--------------------------------------------------------------------------------------------------

i.    	Auditorium						35 – 40

b.	Attenuators  shall be of steel construction with  casings out of minimum 22 G galvanized steel. Acoustic fill shall be inert, non-hygroscopic, vermin proof, fibre glass of required  density adequately protected against  corrosion and  covered  with 26 gage  perforated  aluminium  sheet.  Attenuators shall be supplied complete with flanges.

d.	The  pressure  drop  values of  the  silencers  shall  be indicated for each duty.

e.  	Manufacturers   shall  submit  a  test  certificate   for acoustic and aerodynamic performance of the  attenuators.  Attenuators shall be tested in accordance with ACMA  test methods/BS  4718  and insertion loss and  self  generated noise  for  each octave band and pressure drop  shall  be stated in the schedule.

# C.18	ELECTRICAL INSTALLATION FOR HVAC SYSTEMS

1	SCOPE

The scope of this section comprises of design, fabrication, supply, erection, testing and commissioning of Motor Control Centre (MCC), wiring and earthing of all air-conditioning equipment, components and accessories.

1.1	GENERAL

1.1.1	This Specification covers the general requirements for design, manufacture, testing and supply of Main Distribution Boards (MDB / L.V. Panel). The specific requirements and details of the main distribution board(s) or L.V. Panel(s) required are given on the drawings.

1.1.2	The Contractor shall install the Main Distribution Boards (MDB / L.V. Panel) as shown in the drawings and in full compliance to this specification, the international standards specified in the following section & the local authority regulations. In case of difference between this specification, the specified international standards and the local authority regulations, the more stringent requirements in compliance with local authority regulations shall prevail.

1.2   MANUFACTURER & PANEL BUILDER / ASSEMBLER: PRE-QUALIFICATIONS

1.2.1	Main distribution boards shall be assembled only by the original manufacturer and approved by the consultant. The certificate copy issued by original manufacturer shall be attached with quotation document for review & acceptance.

1.2.2	Panel builder shall have a minimum experience of 10years in the field of manufacturing of TTA /IEC 61439 Design LT Panels.

1.3	APPLICABLE STANDARDS

1.3.1	Unless specified otherwise Main Distribution board / L.V. Panel shall conform in design, material, construction and performance to the latest editions of the International recommendations (IEC standards) and its corresponding British / European standards (BSEN standards) and in particular to the following publications:

-	Low Voltage Switchboard	IEC 61439-1 & 2

-	Degree of protection		IEC 60529

In addition to the above listed standards, the local authority regulations shall also be adhered to.

1.4	SITE CONDITIONS

1.4.1	For general climatic conditions, refer and comply the specified project site conditions. The main distribution boards shall comply and perform satisfactorily.

1.5	 DESIGN CONSIDERATIONS

1.5.1	The main distribution boards shall be of standard, natural air cooled, well tested and proven design which ensures maximum safety to personnel, maximum service reliability and economic operations. Design and construction shall be simple, well laid-out and shall provide good accessibility to components and parts.

1.5.2	Unless specified otherwise, the form of construction for the main distribution board shall comply with Form 3/4 requirements of IEC 61439.

1.5.3	Unless specified otherwise, the main distribution board shall be fixed version with main incoming Air Circuit Breaker shall be withdrawable type and the outgoing MCCB shall be fixed type.

1.5.4	Main distribution boards shall be rated on the basis of voltage, current, frequency and the symmetrical breaking capacity of incorporated switching devices.

1.5.5	The electrical system for all main distribution boards shall be 415V, 50 Hz 3phase and neutral, 4-wire solidly earthed. The main distribution boards shall be suitable for operating voltage up to 690 V and Insulation voltage of 1000V.

1.5.6	Unless specified otherwise, the fault level withstand capacity of the main distribution board bus bar system shall be as mentioned in SLD/BOQ. The type test certificate shall be submitted for consultant Owner/PMC verification, to prove the fault level withstand capacity of the main distribution boards. Even under extreme conditions of short circuit or mal-operation there shall be no danger to persons in the vicinity of the assembly.

1.5.7	All equipment and components of the main distribution boards shall be capable of continuous operation at their full current and voltage ratings and without detriment or malfunction at system continuous deviation of up to and including the following percentages of the normal values.

-	Voltages 	± 10%

-	Frequency	± 5%

All components shall be capable of withstanding the dynamic, thermal and dielectric stresses resulting from prospective short circuit currents without damage or injury to personnel.

1.6	CONSTRUCTION REQUIREMENTS

1.6.1	General

1.6.1.1	The main distribution boards shall be assembled by an approved panel builder, who shall pre-qualify and comply with requirements specified under panel assembler pre-qualification of this specification. The main distribution boards shall be assembled by the same panel builder / assembler, who shall also assemble the sub-main, motor control centre and SUB distribution boards.

1.6.1.2	Unless specified / approved otherwise, enclosure system, the switching devices and other components used for assembly of the main distribution boards shall be from original manufacturer.

1.6.1.3	Unless specified otherwise, the main distribution board shall be of fixed version with cable access at rear/front to have optimal solution.

1.6.1.4	Type test certificates shall be available for the proposed type of enclosure and the busbar system. The type test certificates shall be clearly state type, model and main characteristics of the assembly, references of the standards applied for the tests, results obtained and the observations made during & after the tests..

1.6.1.5	Components shall be as per approved makes.

1.6.1.6	Design drawings, component catalogues and type test certificates shall be submitted for consultant approval prior to placement of order for the main distribution boards.

1.6.1.7Vendor shall ensure components like ACB’s, MCCB’s selected shall have both current and time discriminations. Published coordination chart or coordination study done using switchgear manufacturer’s software shall be furnished along with drawing for approval.

1.6.2	General Arrangement & Assembly

1.6.2.1	L.V Panel shall comprise of free standing enclosure, bus bar system, switching devices such as ACB/MCCB, metering equipments, all necessary current transformers and the like as required. Panel shall be assembled in a systematic manner such as Transformer Incomer section, Generator Incomer section (if applicable), Bus coupler section (if applicable), Incomer Metering / Indication section and Outgoing section.

1.6.2.2	Unless otherwise specified the panels shall be designed to accept bottom/top entry of cables and shall be of rear access type. The rear access shall only be provided for access for termination of cables, all other equipments shall be accessible / operable from the front of panel. Where front access type is specified, the panel shall be designed completely for front access only.

1.6.2.3	Each panel section (cable compartment) shall be provided with thermostatically controlled panel heater in Main Distribution Board.

1.6.2.4	Each section shall be arranged typically as described below and as per the details shown in the drawings:

a      	Incomer section (Transformer Incoming)

Transformer Incomer panel shall be a 3 compartment enclosure with Top & Bottom compartment dedicated for metering / controls and the Middle compartment shall be dedicated for the circuit breaker. It shall comprise of but not limited to the following:

Bottom Compartment

-	Incomer supply cables / bus duct

Middle Compartment

-	Main Incoming circuit breakers with rating and type as per the drawing.

Top Compartment

-	Any control component for Incoming circuit breaker.

-   Digital power meter to indicate various electrical parameters

-   Phase indication lamps wired to the line side of the circuit breaker.

-   Power factor meter (If required as per local authority requirement).

-    KWH energy meter (If location of KWh is approved by local authority).

b    	Incomer section (Generator Incoming) – (If applicable)

Generator Incomer panel shall be a 3 compartment enclosure with Top & Bottom compartment dedicated for metering / controls and the Middle compartment shall be dedicated for the circuit breaker. It shall comprise of but not limited to the following:

Bottom Compartment

-	Incomer supply cables / bus duct

Middle Compartment

-	Main Incoming circuit breakers with rating and type as per the drawing.

Top Compartment

-	Any control component for Incoming circuit breaker.

-   Digital power meter to indicate various electrical parameters

-   Phase indication lamps wired to the line side of the circuit breaker.

-   Power factor meter (If required as per local authority requirement).

-    KWH energy meter (If location of KWh is approved by local authority).

c      	Bus coupler / Bus Tie section – (If applicable)

The Bus Tie / Bus Coupler Panel shall be a 3 compartment enclosure to match with the incomer panels. The Top & Bottom compartment can be used for accommodating the common controls of the incoming and the bus tie circuit breakers. The Middle compartment shall be dedicated for the circuit breaker. It shall comprise of but not limited to the following:

Notes:

-   Where ACB’s are used as incoming or bus coupler, the front face of the ACB shall be accessible for operation from the front without opening the feeder door.

-	Where MCCB’s are used as incoming or bus coupler circuit breakers an Direct Rotary handle shall be provided at the front face of the MCCB which is operated from front door. All such handles shall be door interlocked to ensure safety for operating personnel.

d   	Outgoing section(s)

The outgoing section(s) enclosure shall accommodate the outgoing circuit breakers which shall be arranged in a systematic and symmetrical manner. It shall comprise of but not limited to the following:

Each panel shall have various fixed compartments with individual doors for each compartment and each compartment shall accommodate the following:

-   Circuit breakers with rating and type as specified in the drawings.

-   Any other controls, which may be part of the outgoing circuit breakers along with Indication Lamps & metering as specified in SLD/BOQ.

Notes:

-	All circuit breakers and other controls pertaining to a feeder shall be accommodated in its own compartment, which shall have its own feeder doors. Keys for all such external door shall be common.

-	Moulded case circuit breaker in each compartment shall be equipped with a operating handle extended to the front face of the door for operation. All such door handles shall be door interlocked to ensure safety for operating personnel.

-	Air circuit breaker front face shall be accessible without opening the door.

-	Circuit breakers and other control components shall be fully accessible after opening the panel door; however, no live parts shall be exposed.

-	All the bus bar connections / terminations to the outgoing circuit breakers shall be taken from the rear side of the circuit breaker, which shall be shrouded properly using metallic / poly carbonate sheets. All the MCCB terminals shall be fully shrouded with original terminal shrouds from the MCCB manufacturer, in such a  way that no live parts are exposed, when the front door is opened.

-	Opening of the front door shall give access to the circuit breaker for rating adjustments etc.

-   	Maximum 2 nos. air circuit breakers shall be installed in one vertical, provided that sufficient space for cable termination is provided and de-rating of circuit breaker is carried out as per manufacturer recommendations.

-	Maximum 2 nos. moulded case circuit breakers, rated at 800Amps shall be installed in one vertical, provided that sufficient space for cable termination is provided.

-	Maximum 9 nos. of moulded case circuit breakers (rated less than 250Amps) shall be installed in one vertical, provided that sufficient cable termination is provided.

-	All Partitioning and shrouding shall comply the requirements of Form-3/4, construction as per IEC standards.

1.6.3.1	Main distribution board enclosure shall be product from approved manufacturer. The sheets have a fine surface finish, which gives good presentation to the painted/ Powder Coated components of the enclosure.

1.6.3.2	The enclosure system shall be Modular in nature. Enclosure parts/kits shall be interchangeable to reduce downtime during modification or maintenance work.

1.6.3.3	The enclosure shall be powder coated with paint shade as specified. The painting process shall include removal of moisture on the sheet steel surface using and applying thermosetting polyester powder using Powder Coating guns. Polymerization of the powder shall take place when the components are cured at about 180ºC, forming a continuous integrated coating. A  uniform coating of atleast 70-80 microns shall be provided.

1.6.3.4	The pretreated and powder coated sheet steel components shall be atleast tested randomly at regular intervals for coating thickness measurement, adhesion test, bend test, impact test, hardness test, salt spray test etc & manufacturer must posses the In – House test facilities for the same.

1.6.4.1	Main distribution board manufacturer shall fabricate & assemble the fabricated elements of the enclosure system, busbar system, switching devices and other equipment to complete the main distribution board all the facility shall be IN-HOUSE.

1.6.4.2	Main distribution board enclosure shall be fabricated of minimum 2mm for load bearing members and 1.5mm non-load bearing members with thick electro-galvanized sheet steel folded construction.  The enclosure shall be of simple and robust construction designed for a variety of dimensions obtainable by means of standardized basic elements.

1.6.4.3	The complete assembly shall be rigid self-supporting structure which is deformable and unaffected by vibration/shocks. The structure shall be completed by a metal partition made of one or more pieces between two sections depending on the depth of the compartment. The lower part of structure shall be closed by means of bolted plates that can be removed whenever the assembly of cable glands is required. The switchgear components contained in sections shall be installed on mounting plates. Each door panel shall be equipped with door interlock with MCCB operating handle. All door hinges to be of concealed type and it shall be possible to remove the door panel whenever required. All doors, bolted cover, partitions, mounting plates and metallic shrouds shall be effectively connected to earth. Flexible earth wires shall be used for removable covers and hinged doors. Each vertical shall be provided with common lockable door to prevent unauthorised operation.

1.6.4.4	The structure and the partitions shall be protected by a durable scratch resistant textured paint finish, epoxy powder polymerized at high temperatures to an approved paint shade.

1.6.4.5	Unless specified otherwise, the main distribution board shall be with ingress protection rating of IP as per IEC standards as minimum.

1.6.4.6	Unless specified otherwise, Main distribution boards shall be designed for front access for the purpose of operation and access to all components and shall suit front or rear access for cable connections and top or bottom for cable entries. Wherever required, enclosure shall be suitable for busduct entry at the top. The access and entries shall be provided as per site requirements.

1.6.4.7	Adequate care shall be taken while designing the main distribution board connection spaces for the external cables. Sufficient cable supports shall be provided for routing the cables inside the enclosure.

1.6.4.8	Enclosure system shall effectively dispose the heat produced by the main circuits and shall integrate a high performance natural ventilation system which shall be aimed at regulating the internal temperature based on the actual capacities of the components.

1.6.4.9	Enclosure shall be readily suitable for future extension on either side without any modifications (after installation at site).

1.6.4.10	Form-3/4 construction assembly shall provide protection against contact with internal live parts and components. Bus bar, functional units and cable termination shall be segregated from each other as given below:

-  Bus bar shall be separated from functional units;

-  Functional units/switching devices shall be separated from each other;

- Cable termination and functional units/switching devices shall be separated from each other;

-  Incoming and outgoing terminals shall be separated from each other.

Bus bars shall be accommodated in a separate chamber/alley with metallic/poly carbonate shrouds and partitions to avoid accidental external contacts.

Incoming switching device shall be located in separate section and outgoing switching devices in other sections, wherever applicable. Each switching device shall be segregated from each other and located in individual compartment with hinged door.

External cable termination to the switching device terminals shall be outside the functional unit / switching device compartment. Segregation shall be made between the switching device terminal and the switching device within its compartment by means of rigid barriers and partitions.

All segregation shall be achieved by means of rigid metallic sheet partitions. Segregation and partition shall ensure protection against contact with live parts and limitation of the faults within each of the functional unit compartment.

A cable alley shall be provided either at rear or at the side of each section as per site conditions and requirements to facilitate termination of cables.

Cables shall be glanded on the bottom/top plate of common cable alley/chamber. Supports shall be provided to fasten the power and control cables inside cable alley/chamber.

1.6.5	Bus bars

1.6.5.1	The bus bar system shall be designed as per the pre-defined guidelines provided by the original manufacturer. The bus bar system shall be type tested by the manufacturer at reputed laboratory for short circuit withstand capacity. The neutral and earth bus bars shall also be type tested for the short circuit withstand capacity. The fault level rating of the bus bar system shall be as per the drawings however the minimum short circuit withstand capacity shall be 50KA RMS for 1second.

1.6.5.2	The bus bars shall be of electrolytic grade (E91E or better) aluminium or copper of rectangular shape. The phase bus bars and neutral bus bars shall be arranged systematically in a bus bar chamber/ alley. The bus bars shall be shrouded completely using metallic partitions and/or polycarbonate shrouds as applicable. The bus bar assembly shall be shrouded (at least IP20) by shrouds so that no live parts are accessible.

1.6.5.3	The busbar system shall be supported adequately at regular intervals as per manufacturer guidelines based on the type test results on a specially designed busbar supports. The supports shall be independently fixed to structure to strengthen the busbar arrangement. Wherever required additional intermediate supports shall be provided between the busbars. All vertical droppers shall also be adequately supported as per the manufacturer guidelines and the test results. The distribution busbars shall be connected to the main busbars by suitable sized and graded bolt & nut and contact washers.

1.6.5.4	Distance between the busbar supports for busbar system and the distance between different phases of busbar system shall be as per original manufacturer guidelines based on the type test results.

1.6.5.5	The main busbars shall be accommodated in a separate busbar chamber running horizontally at top or bottom.

1.6.5.6	The dimensioning of the busbar system shall be as per the rated current of the main switching device, the short circuit current, the maximum rated permissible temperature and the ambient temperature around the busbars. The selection of busbars shall be supported by calculations and recommendations from the original manufacturer.

1.6.5.7	The neutral busbar shall run along with the phase busbars and neutral termination for outgoing switching devices shall be provided with bolted link for isolation purpose.

1.6.5.8	Earth busbar shall be running throughout the panel fitted directly on to the structure for connection of the protective conductors to provide equipotential bonding of exposed conductive parts. Earth busbar shall be located at the bottom of the panel and in the cable chamber/ alley to facilitate easy connection of protective conductor.

1.6.5.9    The busbar joints shall be plated or provided with bimetallic washers for dissimilar material. The hardware used at joints shall be as per original manufacturer’s recommendation.

1.6.8	Testing

1.6.8.1	Type test

The main distribution board and the components as applicable preferably highest rating shall be type tested in accordance with the IEC standards to verify the specified fault level withstand capacity from a reputed and approved type testing laboratory.

The following type tests as specified in IEC 61439-1standards shall be carried out on assembly at recognized test laboratories CPRI /ERDA and certificates shall be provided for following test:

1.	Verification of temperature-rise limits (IEC Cl. 10.10);

2.	Verification of the dielectric properties (IEC Cl. 10.9);

3.	Verification of short-circuit withstand strength (IEC Cl. 10.11);

4.	Verification of the effectiveness of the protective circuit (IEC Cl.10.5)

5.	Verification of clearances and creep age distances (IEC C. 10.4)

Type test certificates shall be submitted to the consultant Owner/PMC for verification.

1.6.8.2	Routine test

The panel assembler shall perform the routine test and provide the test certificates as defined in IEC standards. The routine test shall include but not limited to the following:

1.	Inspection of the assembly including inspection of wiring and electrical operational test

2. 	Dielectric test & Insulation resistance test

3.	Checking of protective measures and of the electrical continuity of the protective circuits

4.	 Functional test as per the approved test procedure.

Routine test certificates and test readings shall be submitted to the consultant Owner/PMC for verification.

2.	CONTACTORS: -

a)     Contactors shall be of double break, single throw and electromagnetic and non- gravity type.

b)     Contactors shall be suitable for interrupted duty and shall be rated for class AC-3 duty.

c)     Main contacts of contactors shall be silver faced.

d)  Operating coils of contactors shall be suitable for operation on 220/240VAC, 1 phase, 50Hz supply.

e)   Contactors shall be provided with at least two pairs of 'NO' and 'NC auxiliary contact.

f)   Contactors shall not drop out at voltages down to 70% of coil rated voltages and min pick up voltage 85%.

3.	OVERLOAD RELAYS: -

a)	Over load protection for each motor feeder (wherever required)shall be provided by thermal over load relay on each of the three phases.

b)	The relay shall be duly compensated against fluctuation so ambient temp. and frequency and shall have single phasing preventer feature.

c)	Relay shall be hand reset type from the front of the cubicle door.

Overload relay for fan applications shall be of heavy duty type with provision of by passing the same during starting of the fan.

4.	Moulded Case Circuit Breakers: -

The MCCB’s shall comply with International Standards as per IEC60947-1 and IEC60947-2. All MCCB’s in the Main Distribution Board shall have ultimate short circuit breaking capacity of 50KA at 415 volts. The circuit breakers shall have service short circuit breaking capacity equal to ultimate short circuit breaking capacity.

The short circuit breaking capacity of MCCB’s shall be inline with busbar fault current of the low voltage switchboards. If Switchboard fault current is 50KA, All MCCB’s used in the switchboard shall be of 50KA minimum.

The moulded circuit breakers offered shall strictly comply with environmental protection. The circuit breakers shall be free from hazardous substances like Lead, Mercury, Cadmium, Chrome etc. The materials shall be suitable for recyclability.

Manufacturer shall furnish discrimination chart for coordination between upstream and downstream devices. The MCCB’s shall be from one manufacturer and shall be from one range.

The MCCB’s shall be Line/Load Interchangeable. The MCCB’s shall have adjustable over load settings & adjustable short circuit settings for discrimination. The rated impulse withstand capability shall be minimum of 8kV. The circuit breaker shall comply with the requirement of isolation function in accordance with IEC 60947

The circuit-breakers shall be tropicalized to make them suitable for use in hot-humid places, in compliance with the International IEC 60068-2-30 Standards.

MCCB’s up to 100A shall be of Thermo-magnetic release. MCCB 125A and above shall be Microprocessor based release. The ground fault protection shall be inbuilt and external module for ground fault is not acceptable.

4.1	Thermo-magnetic trip unit should have: -

1-) Adjustable thermalprotectionfrom70– 100%timesthecurrentrating In.

2-) Fixed magnetic protection for current ratings up to100A.

4.2	Electronic trip units should have: -

1-) Adjustable overload protectionfrom40-100%timesthecurrentrating and with time setting.

2-) Variable short circuit protection setting from1 to10 In and with time setting.

3-) Instantaneous protection setting from 1 to 10 In and time setting will be instantaneous trip take place.

4-) Earth Fault protection variable setting and with time setting.

5-) In case of 4 pole MCCB neutral should be adjustable as a Neutral unprotected or neutral.

The MCCB’s offered shall have trip free mechanism. Circuit-breakers fitted with electronic trip units shall comply with International Standards on electromagnetic compatibility.

The moulded-case circuit breakers shall be designed for both vertical and horizontal mounting, without any adverse effect on electrical performance.

The operating mechanism of the moulded-case circuit breakers shall be of the quick-make, quick-break type with fault tripping overriding manual operation. All poles shall operate simultaneously for circuit breaker opening, closing and tripping.

5.	COMPONENTS SPECIFICATION

5.1	Air Circuit Breakers: -

The Air Circuit Breakers shall be rated Service voltage of 690V AC and Insulation Voltage of 1000V AC. The Air Circuit Breaker shall comply with latest international standards IEC60947-2. The Air Circuit Breaker shall be 3/4 Pole Motorised Draw out type capable of handling rated current up to in ambient temperature of 45 deg Celsius.

Air circuit breakers(ACB) shall comply with standards IS/IEC60947-1 &2. The breakers shall be tested & certified at ERDA /CPRI/International Laboratories.

Draw out Circuit Breakers shall have three discrete positions Isolate/Test/Service positions. It shall have visual indication to show position. The Circuit Breaker shall have clear visual indication to show whether it is in closed or open condition. The closing mechanism shall be spring charged mechanism. It shall be possible to visualize whether spring is charged or discharged condition. The stored energy in the spring charged mechanism shall be sufficient to ensure that, it shall be possible to open a circuit breaker, reclose & open again.

CircuitbreakersshallconformtoElectromagneticcompatibilitytests(EMC)asspecifiedin

IEC60947-2.

All ACB’s irrespective incoming or outgoing feeders shall have neutral protection. In case 3Pole ACB are offered based on application, it shall still be possible to protect the neutral by providing an external CT as per BOQ

The Air Circuit Breaker shall have Service Short Breaking capacity of 50ka (Ics) at 440volts AC.  Circuit Breakers with less than 50ka (Ics) is not acceptable.

All ACB shall have Icu=Ics=Icw=50KA or 1sec minimum.

The operating mechanism shall be of the Open/Closed/Open stored-energy spring type.

All 4Pole ACBs shall have fully rated neutral equal to rating of the breaker & shall be protected again stover-load & short-circuit with provisions for settings at neutral for protection, half protection or no protection.

5.2	Protection Release: -

The Circuit breaker protection shall be through micro-processor based trip units.

The micro-processor release should be self-powered type without any auxiliary power supply during normal operation of the breaker.

The circuit breaker control unit shall measure the true r.m.s value of the current.

I2t ON/I2t OFF options shall be available for short-circuit & earth fault protections to enhance discrimination with down stream devices.

The trip unit shall have integral test facility to verify the healthiness and to avoid

external calibration.

The protection release provided shall be microprocessor based. The protection release shall have LSIG protection as standard.

Protection Release shall have rating plug whereby over load setting range can be adopted based on load conditions without modifying any internal components of the Circuit breakers.

1-) Adjustable overload currentsettingsfrom40% to100%ofratingofACB (In). With Overload time setting.

2-) Shortcircuitsettingfrom1 to10 times of Insetting Short circuit time delay adjustable from 0.5 to 0.8 sec.

3-)Instantaneous protection with an adjustable pick-up and an OFF position.

4-) Earth fault setting adjustable with time delay settings.

ACB release shall be able to continuously sense following elements for healthiness if any failure it should be indicated by LED /LCD Display.

The selective short circuit protection shall have setting possibility of either trip time independent of current or with constant specific let through energy. They selection of devices in upstream and downstream shall be such that complete discrimination is achieved.

The protection release shall be suitable to achieve both current and Time discrimination with downstream protection devices. Protection release considered shall have an option to achieve Zone selectivity with which downstream equipment’s and cables are protected against fault current in shortest possible time as per requirement in BOQ.

The protection releases of Air circuit breakers shall have built in data log function.

The communication protocol shall be modbus/any open protocol to interface with upstream BMS/SCADA systems.

All incomer Circuit Breakers shall have following additional features and measurement functions as standard: -

5.3 Protections: -

1.LSIG Protection

Measurements: -

1-) Voltage

2-) Power

3-) Power Factor.

4-) Frequency

5-) Energy

All outgoing ACB shall have additional features as below: -

1-) All outgoing ACB shall have LSIG protection and current metering.

2-) Chronological event storage.

6    Motor Protection Circuit Breaker (MPCB)

Motor circuit breakers shall conform to the general recommendations of standard IEC 947 -1,2 and 4 (VDE 660, 0113 NF EN 60 947-1-2-4, BS 4752) and to standards UL 508 and CSA C22-2 N°14.

The devices shall be in utilization category A, conforming to IEC 947-2 and AC3 conforming to IEC 947-4. MPCB shall have a rated operational and insulation voltage of 690V AC (50 Hz) and MPCB shall be suitable for isolation conforming to standard IEC 60947-2 and shall have a rated impulse withstand voltage (Uimp) of 6 kV. The motor circuit breakers shall be designed to be mounted vertically or horizontally without derating.  Power supply shall be from the top or from the bottom. In order to ensure maximum safety, the contacts shall be isolated from other functions such as the operating mechanism, casing, releases, auxiliaries, etc, by high performance thermoplastic chambers. The operating mechanism of the motor circuit breakers must have snap action opening and closing with free tripping of the control devices. All the poles shall close, open, and trip simultaneously. The motor circuit breakers shall accept a padlocking device in the “isolated” position.

The motor circuit breakers shall be equipped with a “PUSH TO TRIP” device on the front enabling the correct operation of the mechanism and poles opening to be checked. The auxiliary contacts shall be front or side mounting, and both arrangements shall be possible. The front-mounting attachments shall not change the breaker surface area. Depending on its mounting direction the single pole contact block could be NO or NC. All the electrical auxiliaries and accessories shall be equipped with terminal blocks and shall be plug-in type. The motor circuit breakers shall have a combination with the downstream contactor enabling the provision of a perfectly co-ordinated motor-starter. This combination shall enable type 1 or type 2 co-ordination of the protective devices conforming to IEC 60947-4-1. Type 2 co-ordination shall be guaranteed by tables tested and certified by an official laboratory: LOVAG (or other official laboratory).The motor circuit breakers, depending on the type, could be equipped with a door-mounted operator which shall allow the device setting. The motor circuit breakers shall be equipped with releases comprising a thermal element assuring overload protection and a magnetic element for short-circuit protection. In order to ensure safety and avoid unwanted tripping, the magnetic trip threshold (fixed) shall be factory set to an average value of 12 Ir.

All the elements of the motor circuit breakers shall be designated to enable operation at an ambient temperature of 60°C without derating. The thermal trips shall be adjustable on the front by a rotary selector. The adjustment of the protection shall be simultaneous for all poles. Phase unbalance and phase loss detection shall be available. Temperature compensation (-20°C to +60°C)

7   MINIATURE CIRCUIT BREAKER (MCB)

Miniature Circuit Breaker shall comply with IS-8828-1996/IEC898-1995. Miniature circuit breakers shall be quick make and break type for 240/415 VAC 50 Hz application with magnetic thermal release for over current and short circuit protection. The breaking capacity shall not be less than 10 KA at 415 VAC. MCBs shall be DIN mounted. The MCB shall be Current Limiting type (Class-3). MCBs shall be classified (B,C,D ref IS standard) as per their Tripping Characteristic curves defined by the manufacturer. The MCB shall have the minimum power loss (Watts) per pole defined as per the IS/IEC and the manufacturer shall publish the values.MCB shall ensure complete electrical isolation & downstream circuit or equipment when the MCB is switched OFF.

The housing shall be heat resistant and having a high impact strength. The terminals shall be protected against finger contact to IP20 Degree of protection. All DP, TP, TPN and 4 Pole miniature circuit breakers shall have a common trip bar independent to the external operating handle.

8   LABELS

Engraved PVC labels shall be provided on all incoming and  outgoing  feeder.  Circuit diagram showing the  arrangements  of  the circuit inside the control panel  shall  be pasted  on inside of the panel door and covered with  transparent plastic sheet.

9   STARTERS

Each motor shall be provided with a starter  of suitable  rating.   Starters shall be in  accordance  with relevant  IS Codes.  All Star Delta Starters shall be fully automatic. Motors up to 10HP shall be provided by Direct On Line (DOL) starter, motors above 10 HP and up to 45 HP shall be provided by star/delta starter and motors above 45 HP shall be provided by soft starter.

10	CONTACTOR

Contactor shall be built into a high strength thermoplastic body and shall be provided with an arc shield for quick arc extinguishing. Silver alloy tips shall be provided to ensure a high degree of reliability and endurance under continuous operation. The magnet system shall consist of laminated yoke and armature to ensure clean operation without hum or chatter.

Starters contactors shall have 3 main and 2 Nos. NO / NC auxiliary contacts and shall be air break type suitable for making and breaking contact at minimum power factor of 0.35.  For design consideration of contactors the starting current of connected motor shall be assumed to be 6 times the full load current of the motor in case of  direct-on-line  starters  and 3 times the full load current  of  the motor  in case of Star Delta and  Reduced  Voltage  Starters.  The insulation for contactor coils shall be of Class “E”.

Coil shall be tape wound vacuum impregnated and shall be housed in a thermostatic bobbin, suitable for tropical conditions and shall withstand voltage fluctuations. Coil shall be suitable for 220/415±10%  volts AC, 50 cycles AC supply.

11	THERMAL OVERLOAD RELAY

Thermal over load relay shall have built in phase  failure sensitive tripping mechanism to prevent against single phasing as well as on overloading. The relay shall operate on the differential system of protection to safeguard against three phase overload, single phasing and unbalanced voltage conditions.

Auto-manual conversion facility shall be provided to convert from auto-reset mode to manual-reset mode and vice-versa at site. Ambient temperature compensation shall be provided for variation in ambient temperature from -5° C to +55°C.

All overload relays shall be of  three   element,  positive  acting   ambient   temperature compensated  time  lagged  thermal over load  relays  with adjustable  setting.  Relays shall be  directly  connected for  motors  upto 35 HP capacity.   C.T.  operated  relays shall be provided for motors above 35 HP capacity.  Heater circuit  contactors  may  not be  provided  with  overload relays.

12	TIME DELAY RELAYS

Time delay relays shall be  adjustable type  with  time delay adjustment from 0-180  seconds  and shall  have one set of auxiliary contacts for  indicating lamp connection.

13	INDICATING  LAMP AND METERING

All meters and  indicating lamps  shall be in accordance with relevant IS standard specification.   The meters  shall be flush mounted  type. The indicating  lamp shall  be   of  LED type . Each  MCC and control  panel  shall  be provided with voltmeter 0-500 volts with three way and off selector switch, CT operated ammeter of suitable range with three  nos. CTS of suitable ratio with three way  and  off selector   switch,  phase  indicating  lamps,  and   other indicating  lamps  as called for.  Each  phase  indicating lamp  shall  be  backed  up  with  5  amps  fuse.    Other indicating  lamps shall be backed up with fuses as  called for in Technical Specification.

14	TOGGLE  SWITCH

Toggle switches, as per technical specifications shall be in conformity with relevant IS Codes and shall be of 5 amps rating.

15	PUSH BUTTON STATIONS

Push button  stations  shall  be  provided  for  manual starting and stopping  of  motors  /  equipment Green and Red colour push  buttons shall   be   provided  for   ‘Starting’   and   ‘Stopping’ operations. ‘Start’ or ‘Stop’ indicating flaps shall  be provided for push buttons.  Push Buttons shall be suitable for  panel  mounting  and accessible  from  front  without opening door, Lock lever shall be provided for ‘Stop’ push buttons.  The push button contacts shall be suitable for 6 amps current capacity.

16	CONDUITS

Conduits  and  Accessories shall  conform  to  latest edition of Indian Standards IS-9537 part 1 & 2.  16/14 (16 gauge upto 32mm diameter  & 14 gauge above 32 mm diameter) gauge screwed GI or MS conduits as specified on Technical Specification shall be used.  Joints between  conduits  and accessories shall be securely made by standard accessories, as per IS-2667, IS-3837 and IS-5133 to ensure earth continuity. All conduit accessories shall be threaded type only.

Only approved make of conduits and accessories shall  be used.

Conduits  shall be delivered to the site of  construction  in original  bundles and each length of conduit shall bear the  label of the  manufacturer.

Note. : Whatever materials billed by the Contractor should come on site with proper Challan  Numbers and quantity mentiond in each such Challan..

Maximum permissible number of  1100 volt grade PVC insulated wires that may be drawn into metallic Conduits are given below :

| Size of wires Nominal Cross | Maximum number of wires within conduit size(mm) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| section Area (Sq. mm.) | 20 | 25 | 32 | 40 | 50 |
| 1.5 | 5 | 10 | 14 | -- | -- |
| 2.5 | 5 | 8 | 12 | -- | -- |
| 4 | 3 | 7 | 10 | -- | -- |
| 6 | 2 | 5 | 8 | -- | -- |
| 10 | -- | 3 | 5 | 6 | -- |
| 16 | -- | 2 | 3 | 6 | 6 |
| 25 | -- | -- | 2 | 4 | 6 |
| 35 | -- | -- | -- | 3 | 5 |

Maximum permissible number of  1100 volt grade PVC insulated wires that may be drawn into rigid non metallic or PVC Conduits are given below :

| Size of wires Nominal Cross | Maximum number of wires within conduit size(mm) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| section Area (Sq. mm.) | 20 | 25 | 32 | 40 | 50 |
| 1.5 | 7 | 12 | 16 | -- | -- |
| 2.5 | 5 | 10 | 14 | -- | -- |
| 4 | 4 | 8 | 12 | -- | -- |
| 6 | 3 | 6 | 8 | -- | -- |
| 10 | -- | 4 | 5 | 6 | -- |
| 16 | -- | 3 | 3 | 6 | 6 |
| 25 | -- | -- | 2 | 4 | 6 |
| 35 | -- | -- | -- | 3 | 5 |

17    CABLES

The MV cables shall be cross linked polyethylene (XLPE) insulated PVC inner sheathed and HR PVC / FRLS PVC outer sheath of 1100 volts grade as asked for in the Technical Specification.  Cables upto 16 sq.mm shall be with copper conductor and 25 sq.mm and above shall be with aluminium conductor and suitable  for  laying  in  trenches,  ducts,  and on cable trays  as  required.   M.V. Cables  shall  be termite resistant.  Cable glands shall be double compression glands. Control  cables  and  indicating panel cables shall be multi core PVC  insulated copper conductor and armoured cables.

18	CABLE LAYING

Cables shall be laid by  skilled  and  experienced workmen  using  adequate  rollers to minimize  stretching  of  the cable.  The cable drums shall be placed on jacks before  unwinding the  cable.   Great care shall be exercised in  laying  cables  to avoid forming kinks.

18.1 Laying of Cables on Cable Trays

The relative position of the cables, laid on the  cable tray shall be preserved and the cables shall not  cross each other.  At all changes in direction in horizontal and  vertical planes, the cable shall be bent smooth with a radius as recommended by the manufacturer’s. All  cables shall be laid with minimum one diameter gap and  shall be clamped at every metre to the cable tray. Cables shall be tagged  for  identification  with  aluminum  tag  and  clamped properly at every 20M.  Tags shall be provided at both ends and all changes  in directions both sides of wall and floor crossings. All cable shall be identified by embossing on the tag the size of the cable, place of origin and termination.

All cables passing through holes in floor or walls shall be sealed with  fire  retardant  Sealant and  shall be   painted  with  fire retardant  paint  upto one meter on  all joints, terminations  and both sides of the wall crossings by “VIPER CABLE RETARD”.

18.2	Laying of Cables in Ground

The width of  trench  for  laying single  cable shall be minimum 350 mm.  Where more than one cable is to be laid in horizontal formation, the width of the trench shall be workout by providing 200 mm gap between the cables, except where otherwise specified.  There shall be clearance of 150 mm between the end cable and the side wall of the trench.  The minimum depth of the cable trench shall not be less than 750 mm for single layer of cables.  When the cables are laid in more than one tier the depth of the trench shall be increased by 300 mm for each additional tier.

Excavation of trenches   :   The  trenches   shall   be excavated in reasonably straight lines.  Wherever there is  a change in direction, suitable curvature shall  be  provided.   Where  gradients and changes in  depth  are  unavoidable, these shall be gradual.   The excavated soil shall be stacked firmly by the  side  of  the trench such that it may not fall back into  the trench.   The bottom of the trench shall be  levelled  and shall be made free from stone, brick bats etc.  The trench shall then be provided with a layer of clean, dry sand cushion  of not  less than 100 mm in depth. Prior to laying of cables, the  cores  shall  be  tested   for continuity  and insulation resistance.  The cable  drum shall be properly mounted on jacks,  at  a suitable location, making sure that the  spindle, jack etc. are strong enough to carry the weight of  the  drum and the spindle is horizontal.  Cable shall  be  pulled  over  rollers  in  the trench  steadily  and  uniformly without  jerks  and strains.  The entire  drum length  shall  be laid in one  stretch.   However,  where this is not possible the  remainder  of the  cable shall  be removed by `Flaking’ i.e.  by  making  one  long  loop in the reverse  direction.   After  the  cable  has been uncoiled and laid into the trench  over the rollers, the cable shall be lifted off  the rollers beginning  from one end by helpers standing about 10  meters apart and laid in a  reasonably  straight  line.  Cable laid in trenches in a single tier formation shall have a cover of clean, dry sand of not less than  150 mm. above the base cushion of sand before the protective  cover  is laid.  In the  case  of  vertical multi-tier  formation  after the first cable  has  been laid,  a sand cushion of 300 mm shall be provided  over  the  initial  bed before the second tier is  laid.   Finally the cables shall be protected by second class bricks before back filling the trench. The buried depth of uppermost layer of cable shall not be less than 750mm.

Back Filling  : The trenches shall be back filled  with  excavated  earth free from stones or other  sharp  edged  debris  and shall be rammed and watered, if  necessary,  in  successive  layers  not exceeding  300 mm.   Unless  otherwise specified, a crown of earth not less than  50 mm in the centre and tapering towards the sides of  the trench shall be left to allow for subsidence.

19	WIRE AND WIRE SIZES

1100  volts grade PVC  insulted  copper  conductor  wires in conduit shall be used.

For all single phase/ 3 phase wiring, 1100 volts grade PVC insulated  copper  conductor  FRLS/ZHFR wires shall  be used. The equipment  inside  plant  room  and  AHU  room  shall   be connected to the control panel by  means  of  insulated copper  conductor  wires  of  adequate  size  in exposed conduits.   Final  connections to the equipment  shall  be through  wiring enclosed in galvanized  flexible  conduits rigidly  clamped  at  both ends and at regular intervals.   An  isolator  shall  be provided   near   each   motor/equipment   wherever    the motor/equipment is separated from the supply panel through a partition barrier or through ceiling construction.  PVC insulated copper conductor wires  shall  be used  inside  the control panel for  connecting  different components  and  all the wires inside  the  control  panel shall  be  neatly  dressed  and  plastic  beads  shall  be provided  at  both  the ends for  easy  identification  of control wiring.

The minimum size of control wiring shall be 1.5 sq. mm  PVC insulated stranded soft drawn copper conductor wires drawn through  conduit to be provided for  connecting  equipment and control panels.

Power wiring, cabling shall be of the following sizes:

i.    	Upto 5 HP motors/ 5 KW  heaters       	3 x 4 sq. mm copper conductor wires.

ii.   	From 6 HP to 10 HP motors      		3 x 6 sq. mm copper

6 KW to 7.5 KW heaters         		conductor wires.

iii.  	From 12.5 HP to 15 HP          		2 Nos. 3 x 6 sq. mm

motors                         			copper conductor wires

iv.   	From 20 HP to 25 HP motors         		2 Nos. 3 x 10 sq. mm copper conductor

wires

v.    	From 30 HP to 35 HP            		2 nos. 3 x 16 sq. mm

motors                         			aluminium conductor

armoured cable.

vi.   	From 40 HP to 50 HP            		2 Nos. 3 x 25 sq. mm.

motors                         			aluminium conductor

armoured cable.

vii.   	From 60 HP to 75 HP motors     		1 No. 3 x 70 sq. mm

aluminium conductor

armoured cable.

viii.  	100 HP motors                  			1 No. 3 x 150 sq. mm.

aluminium conductor

armoured cable

ix.   	150 HP motor                   			1 No. 3 x 240 sq. mm.

aluminium conductor

armoured cable.

x.    	250 HP motor                   			2 Nos. 3 x 240 sq. mm.

aluminium conductor

armoured cable.

xi.   	400 HP motor                   			3 Nos. 3 x 240 sq. mm.

aluminium conductor

armoured cable.

xii.  	600  HP  motor                 			3 Nos. 3 x 400 sq. mm.

aluminium conductor

armoured cable.

All  the  switches,  contactors,  push  button   stations, indicating  lamps shall be distinctly marked with a  small description  of  the  service  installed.   The  following capacity contactors and overload relays shall be  provided for  different  capacity motors or as  per  manufacturer’s recommendation.

-----------------------------------------------------------------------------------------------------------------

TYPE OF       		CONTACTOR      OVERLOAD

STARTER       		CURRENT            RELAY

CAPACITY           RANGE

-----------------------------------------------------------------------------------------------------------------

5    HP Motors  	D O L         		16 amps         	6-10  amps

7.5 HP motors       	D O L         		16 amps         	9-15  amps

10    HP Motors        	D O L         		25 amps         	9-15  amps

12.5 HP Motors      	Automatic Star Delta   	16 amps         	9-15  amps

15    HP Motors        	Automatic Star Delta    	25 amps         	9-15  amps

20    HP Motors        	Automatic Star Delta    	32 amps         	14-23 amps

25    HP Motors        	Automatic Star Delta    	32 amps         	14-23 amps

30    HP Motors        	Automatic Star Delta   	40 amps         	20-33 amps

35    HP Motors        	Automatic Star Delta    	40 amps         	20-33 amps

40    HP Motors        	Automatic Star Delta    	40 amps         	30-50 amps

50    HP Motors        	VFD / soft		70 amps         	30-50 amps

60    HP Motors           	VFD/ soft		110 amps        	30-50 amps

75    HP Motors           	VFD / soft      		110 amps        	90-150 amps

100    HP Motors          	VFD / soft    		200 amps        	CT operated relay

125    HP Motors          	VFD / soft     		200 amps           	CT operated relay

150    HP Motors          	VFD / soft		200 amps           	CT operated relay

150    HP Motors       	VFD / soft		300 amps           	CT operated Relay.

200    HP Motors          	VFD / soft  		300 amps           	CT operated Relay.

250    HP Motors          	VFD / soft      		400 amps           	CT operated Relay.

300    HP Motors          	VFD / soft    		400 amps           	CT operated Relay.

400    HP Motors          	VFD / soft  		600 amps           	CT operated Relay.

600    HP Motors          	VFD / soft   		900 amps           	CT operated Relay.

Two speed motors when specified, shall be provided with DOL starter irrespective of it rating.

20	CABLE TRAYS

Ladder and perforated type Cable Trays shall be of Hot dip Galvanized type and factory fabricated out of CRCA sheet with standard accessories like tee, bends, couplers etc. for different loads and number and size of cables as given below:

Cable trays shall be galvanized as per Specifications..

a.	1500 mm wide

Runners 25 x 100 x 25 x 3 mm

Rungs 2# 20 x 40 x 20 x 3 mm 250 mm C/C

Suspenders 2 Nos. 40 x 40 x 5 mm GI angle 1500 mm C/C with base support of 40x 40 x 5mm GI angle.

b.	1200 mm wide

Runners 25 x 100 x 25 x 3 mm

Rungs 2# 20 x 40 x 20 x 3 mm 250 mm C/C

Suspenders 2 Nos. 40 x 40 x 5 mm GI angle 1500 mm C/C with base support of 40x 40 x 5mm GI angle.

- 1000 mm wide

Runners 25 x 100 x  25 x 3 mm

Rungs 2# 20 x 40 x 20 x 3 mm 250 mm C/C

Suspenders 2 Nos. 40 x 40 x 5 mm GI angle 1500 mm C/C with base support of 40x 40 x 5mm GI angle.

- 750 mm wide

Runners 20 x 75 x 20 x 2.5 mm

Rungs 20 x 30 x 20 x 2.5 mm 250 mm C/C

Suspenders 2 Nos. 32 x 32 x 5 mm GI angle 1800 mm C/C with base support of 40x 40 x 5mm GI angle.

e	600 mm wide

Runners 20 x 75 x 20 x 2.5 mm

Rungs 20 x 30 x 20 x 2.5 mm 250 mm C/C

Suspenders 2 Nos. 32 x 32 x 5 mm GI angle 1800 mm C/C with base support of 40x 40 x 5mm GI angle.

- 450 mm wide

Runners 20 x 75 x 20 x 2.5 mm

Rungs 20 x 30 x 20 x 2.5 mm 250 mm C/C

Suspenders 2 Nos. 25 x 25 x 4 mm GI angle 1800 mm C/C with base support of 40x 40 x 5mm GI angle.

g.	Supply and fixing of perforated type cable trays of the following sizes of pre-galvanized iron.

i.	600 x 40 x 40 x 2 mm thick

i.	450 x 40 x 40 x 2 mm thick

i.	300 x 40 x 40 x 2 mm thick

ii.	150 x 40 x 40 x 2 mm thick

Note : Suitable length of 10 mm dia GI rod suspenders at 1800 mm interval shall be included in the item for perforated type cable tray.

21	Specification for Hot Dip Galvanizing Process

(for Mild Steel Used For Earthing, Cable Trays Or Junction Boxes  For Electrical Installation.)

General Requirements

I.	Quality of Zinc

Zinc  to   be  used  shall  conform to minimum Zn 98 grade as per requirement of IS:209-1992.

II.	Coating Requirement

Minimum weight  of zinc coating for mild steel flats with thickness upto 6 mm in accordance with IS:6745-1972 shall be 400 g/sqm.

The weight of coating expressed in grams per square metre shall be calculated by dividing the total weight of Zinc by total area (both sides) of the coated surface.

The Zinc coating shall be uniform, smooth and free from imperfections as flux, ash and dross inclusions, bare patches black spots, pimples, lumpiness, runs, rust stains bulky white deposits, blisters.

Mild steel flats / wires shall undergo a process of degreasing pickling in acid, cold rinsing and then galvanizing.

22	Fire retardant Cable Paint & Fire Barrier

The fire retardant paint / barrier shall be listed by independent test agencies such as UL, FM or OPL and be tested to, and pass the criteria of ASTM E 814 ( UL1479) standard test method for fire test through- penetration fire stops and ASTM E 1996 ( UL 2079) standard test method for fire resistive joint system/

22.1     Fire retardant cable Paint

The Fire resistant cable coating / painting shall be intumescent / ablative, water based

compound, The coating shall expand up to 10 times, supplied in a manufacturer seal container indicating manufacturing and expiry dates. The coating material shall be non-toxic, asbestos free, & halogen free and shall have good mechanical strength. The colour of paint shall be white and density of coating shall be 1.3kg/ltr , coating shall have a snap time of 30 minutes, the expansion shall begin at 230 deg.C and it shall have a oxygen index of 41%.

Coating shall be applied by ordinary paint brush after cleaning the cables of dust and oil

deposition. A minimum textured finish of 3 mm wet film thickness shall be achieved by applying the material in 2-3 layers leaving intervals of 2 to 8 hours depending upon the moisture and thickness, moisture and temperature hours between each coat.

22.2   FIRE BARRIER SHEET FOR FLOOR AND WALL SEALING

The framing & fixing part of fire barrier sheet shall be very simple & directly fixed around walls & floors by help of anchored bolts & washer. For 2 hour fire rating the fire barrier sheet shall be minimum 7.62 mm thick and shall be cut as per the profile of penetration and opening. The small gap left around the penetration shall be closed with fire rated soft & mouldable putty. Fire barrier must be design on the intumescent technology to seal larger penetration through the fire rated walls & floors.Fire barrier must be a composite construction with the quality incorporated with organic/ inorganic fire resistive elastomeric sheet with specific gravity of 1.6 gm/ cubic centimeter.

23	TESTING OF CABLES

Cables shall be tested at works for all routine tests as per IS including the following  tests  before being dispatched to site by  the  project team.

- Insulation  Resistance Test.

- Continuity resistance test.

- Sheathing continuity test.

- Earth test.(in armoured cables)

- Hi Pot Test.

Test shall also be conducted at site for insulation between phases and between phase and earth for each length of cable, before and after jointing.   On completion of cable laying work, the following tests shall be conducted in the presence of the Owner/PMC-in-charge.

- Insulation  Resistance Test( Sectional and overall)

- b)	Continuity resistance test.

c)	Sheathing continuity test.

d)	Earth test.

All  tests shall be carried out in accordance with relevant  Standard   Code  of Practice and Electricity  Rules.   The  Contractor shall  provide  necessary instruments, equipment  and  labour  for    conducting the above tests and shall bear all expenses in  connection  with  such  tests.  All tests shall be carried  out  in  the presence of the Owner/PMC-in-charge, results will be noted and signed by all present and record be maintained.

24	EARTHING

Earthing shall be provided  in accordance with IS : 3043 – 1987 and shall  be   copper  strips /wires .The  main  panel  shall  be connected  to  main earthing system of the power  supply.  All single phase metal clad switches and control panels be earthed with minimum 3 mm diameter copper conductor wire.  All 3 phase motors and equipment shall be earthed with 2 numbers  distinct and independent copper wires / tapes as follows:

i.   	Motor upto and including     		2 Nos. 3 mm dia copper

10 HP rating.                  			wires.

ii.  	Motor 12.5 HP to 40 HP        		2 Nos. 4 mm dia copper

capacity.                      			wires.

iii.	Motor 50 to 75 HP capacity.   		2 Nos. 6 mm dia copper

iv.  	Motor above 75 HP.            		2 Nos. 25 mm x 3 mm

copper tapes.

All  switches shall be earthed with two numbers  distinct  and independent copper wires’ tapes as follows:

i.  	3 phase switches               			2 nos. 3 mm dia copper

and control panels upto         		wires.

60 amps rating.

ii.  	3 phase switches, and           		2 Nos. 4 mm dia copper

control panels 63 amps to       		wires.

100 amps rating.

iii.  	3 phase switches and control    		2 Nos. 6 mm dia copper

panels 125 amps to              		wires.

200 amps rating.

iv.  	3 phase switches, control      		2 Nos. 3 mm x 25 mm

panels, bus ducts, above        		copper tapes.

200 amps rating.

The  earthing  connections shall be tapped off from  the  main earthing  of  electrical  installation.   The  overlapping  in earthing  strips at joints where required shall be minimum  75 mm. These  straight  joints shall be  riveted  with  brass rivets & brazed in approved manner.  Sweated lugs of  adequate capacity and size shall be used for all termination of  wires.  Lugs shall be bolted to the equipment body to be earthed after the  metal body is cleaned of paint and other oily  substance, and properly tinned.

25	DRAWINGS

Shop  drawings  for control panels  and  for wiring  of equipment  showing  the  route  of  conduit  & cable  shall   be submitted  by the contractor for approval of Owner/PMC  before starting  the fabrication of panel and starting the work.   On completion,  four  sets of  complete  “As-installed”  drawings incorporating  all  details like, conduits routes,  number  of wires in conduit, location of panels, switches,  junction/pull boxes  and  cables  route  etc.  shall  be  furnished  by  the Contractor.

26	TESTING

Before  commissioning  of the  equipment,  the  entire electrical  installation  shall be tested in  accordance  with relevant  BIS codes and test report furnished by  a  qualified and  authorised  person.  The entire  electrical  installation shall   be  gotten  approved  by  Electrical  Inspector   and   a certificate from Electrical Inspector shall be submitted.  All tests  shall  be carried out in the presence of Owner/PMC-in-charge. Testing of the panels shall be as per relevant BIS Codes :

27  	PAINTING

All  sheet steel work shall undergo a  process  of degreasing,  thorough  cleaning,  and  painting  with  a  high  corrosion  resistant primer.  All panels shall then be  baked in  an oven.  The finishing treatment shall be by  application of  powder coating of approved shade.

28	RUBBER MAT

Rubber mat shall be provided in front to cover the full length of all panels. Where back space is provided for working from the rear of the panel, rubber mat shall also be provided at the back of the panel also to cover the full length of panel. Rubber mats provided shall be as per IS 15652-2006

# C.19	VARIABLE FREQUENCY DRIVES FOR HVAC SYSTEMS

1	GENERAL REQUIREMENTS

  - This specification covers complete variable frequency drives (VFDs) designated on approved drawings to be variable speed. All standard and optional features shall be included within the VFD.

  - The frequency converter shall not be a general purpose product, but a dedicated HVAC Owner/PMCed product.

  - The VFD and its options shall be factory mounted and tested as a single unit under full load before dispatch.

  - The VFD shall be tested to UL 508C. The appropriate UL label shall be applied.

  - The VFD shall be CE marked and conform to the European Union Electro Magnetic Compatibility directive.

  - The VFD shall be UL listed for a short circuit current rating of 100 kA and labelled with this rating.

2	TECHNICAL REQUIREMENTS

2.1	The VFD shall convert incoming fixed frequency three-phase AC power into an adjustable frequency and voltage for controlling the speed of three-phase AC motors. The motor current shall closely approximate a sine wave. Motor voltage shall be varied with frequency to maintain desired motor magnetization current suitable for the driven load and to eliminate the need for motor derating.

When properly sized, the VFD shall allow the motor to produce full rated power at rated motor voltage, current, and speed without using the motor's service factor. VFDs utilizing sine weighted/coded modulation (with or without 3rd harmonic injection) must provide data verifying that the motors will not draw more than full load current during full load and full speed operation.

2.2	VFD shall be installed within panel, suitable for operating conditions.

2.3	The VFD shall include an input full-wave bridge rectifier and maintain a fundamental (displacement) power factor near unity regardless of speed or load.

2.4	The VFD shall have a dual 5% impedance DC link reactor (harmonic filters) on the positive and negative rails of the DC bus to minimize power line harmonics &protect the VFD from power line transients, alongwith advance harmonics filters at integral component of VFD to maintain TH id < 5% at drive terminals to meet IEEE 519, 1992 guidelines.

2.5	VFDs with saturating (non-linear) DC link reactors shall require an additional 3% AC line reactor to provide acceptable harmonic performance at full load, where harmonic performance is most critical.

IEEE519, 1992 recommendations shall be used for the basis of calculation of total harmonic distortion (THD) at the point of common coupling (PCC). On request VFD manufacturer shall provide THD figures for the total connected load. The contractor shall provide details of supply transformer rating, impedance, short circuit current, short circuit impedance etc to allow this calculation to be made.

2.6	All VFDs shall contain integral EMC Filters to attenuate Radio Frequency   Interference conducted to the AC power line. The VFDs shall comply with the emission and immunity requirements of IEC 61800-3 : 2004, Category C1 with 50m motor cable (unrestricted distribution). The suppliers of VFDs shall include additional EMC filters if required to meet compliance to this requirement.

2.7   	The VFD’s full load output current rating shall meet or exceed the normal rated currents of standard IEC induction motors. The VFD shall be able to provide full rated output current continuously, 110% of rated current for 60 seconds and 120% of rated torque for up to 0.5 second while starting.

2.8	The VFD shall provide full motor torque at any selected frequency from 20 Hz to base speed while providing a variable torque V/Hz output at reduced speed. This is to allow driving direct drive fans without high speed derating or low speed excessive magnetization, as would occur if a constant torque V/Hz curve was used at reduced speeds.  Breakaway current of 160% shall be available.

  - A programmable automatic energy optimization selection feature shall be provided as standard in the VFD. This feature shall automatically and continuously monitor the motor’s speed and load to adjust the applied voltage to maximize energy savings.

2.10	The VFD must be able to produce full torque at low speed to operate direct driven fans.

2.11	Output power circuit switching shall be able to be accomplished without interlocks or damage to the VFD.

2.12	An Automatic Motor Adaptation algorithm shall measure motor stator resistance and reactance to optimize performance and efficiency. It shall not be necessary to run the motor or de-couple the motor from the load to perform the test.

2.13	Galvanic isolation shall be provided between the VFD’s power circuitry and control circuitry to ensure operator safety and to protect connected electronic control equipment from damage caused by voltage spikes, current surges, and ground loop currents. VFDs not including either galvanic or optical isolation on both analog I/O and discrete digital I/O shall include additional isolation modules.

2.14	VFD shall minimize the audible motor noise through the used of an adjustable carrier frequency. The carrier frequency shall be automatically adjusted to optimize motor and VFD operation while reducing motor noise. VFDs with fixed carrier frequency are not acceptable.

2.15	The VFD shall allow up to at least 100 meters of SWA (Single Wire Armour) cable to be used between the FC and the motor and allow the use of MICS (Mineral Insulated Copper Sheath) cable in the motor circuit for fire locations.

3 	PROTECTIVE FEATURES

3.1	A minimum of Class 20 I2t electronic motor overload protection for single motor applications shall be provided. Overload protection shall automatically compensate for changes in motor speed.

3.2	Protection against input transients, loss of AC line phase, output short circuit, output ground fault, over voltage, under voltage, VFD over temperature and motor over temperature. The VFD shall display all faults in plain language. Codes are not acceptable.

3.3	Protect VFD from input phase loss. The VFD should be able to protect itself from damage and indicate the phase loss condition. During an input phase loss condition, the VFD shall be able to be programmed to either trip off while displaying an alarm, issue a warning while running at reduced output capacity, or issue a warning while running at full commanded speed. This function is independent of which input power phase is lost.

3.4	Protect from under voltage. The VFD shall provide full rated output with an input voltage as low as 90% of the nominal. The VFD will continue to operate with reduced output, without faulting, with an input voltage as low as 70% of the nominal voltage.

3.5	VFD shall include current sensors on all three output phases to accurately measure motor current, protect the VFD from output short circuits, output ground faults, and act as a motor overload. If an output phase loss is detected, the VFD will trip off and identify which of the output phases is low or lost.

3.6	If the temperature of the VFD’s heat sink rises to 80C, the VFD shall automatically reduce its carrier frequency to reduce the heat sink temperature. It shall also be possible to program the VFD so that it reduces its output current limit value if the VFD’s temperature becomes too high.

3.7	In order to ensure operation during periods of overload, it must be possible to program the VFD to automatically reduce its output current to a programmed value during periods of excessive load. This allows the VFD to continue to run the load without tripping.

3.8	The VFD shall have temperature controlled cooling fan(s) for quiet operation, minimized losses, and increased fan life. At low loads or low ambient temperatures, the fan(s) may be off even when the VFD is running.

3.9	Protect from output switching : The VFD shall be fully protected from switching a contactor / isolator at the output with out causing tripping e.g.:  for switching on/off the isolators of the AHU / ventilation fans / pumps near the motor with VFD in ON mode.

3.10	The VFD shall store in memory the last 10 alarms. A description of the alarm, and the date and time of the alarm shall be recorded.

  - When used with a pumping system, the VFD shall be able to detect no-flow situations, dry pump conditions, and operation off the end of the pump curve. It shall be programmable to take appropriate protective action when one of the above situations is detected.

4 	INTERFACE FEATURES

4.1	Hand, Off and Auto keys shall be provided on the control panel to start and stop the VFD and determine the source of the speed reference. It shall be possible to either disable these keys or password protect them from undesired operation.

4.2	There shall be an “Info” key on the keypad.  The Info key shall include “on-line” context sensitive assistance for programming and troubleshooting.

4.3	The VFD shall be programmable to provide a digital output signal to indicate whether the VFD is in Hand or Auto mode. This is to alert the Building Automation System whether the VFD is being controlled locally or by the Building Automation System.

4.4	Password protected keypad with alphanumeric, graphical, backlit display can be remotely mounted. Two levels of password protection shall be provided to guard against unauthorized parameter changes.

4.5	All VFDs shall have the same customer interface. The keypad and display shall be identical and interchangeable for all sizes of VFDs.

4.6	To set up multiple VFDs, it shall be possible to upload all setup parameters to the VFD’s keypad, place that keypad on all other VFDs in turn and download the setup parameters to each VFD. To facilitate setting up VFDs of various sizes, it shall be possible to download from the keypad only size independent parameters. Keypad shall provide visual indication of copy status.

4.7	Display shall be programmable to communicate in multiple languages including English, Chinese, Korean, Japanese, Thai and Indonesian.

4.8	A red FAULT light, a yellow WARNING light and a green POWER-ON light shall be provided. These indications shall be visible both on the keypad and on the VFD when the keypad is removed.

4.9	A quick setup menu with factory preset typical HVAC parameters shall be provided on the VFD. The VFD shall also have individual Fan, Pump, and Compressor menus specifically designed to facilitate start-up of these applications.

4.10	A three-feedback PID controller to control the speed of the VFD shall be standard.

4.11	This controller shall accept up to three feedback signals. It shall be programmable to compare the feedback signals to a common setpoint or to individual setpoints and to automatically select either the maximum or minimum deviating signal as the controlling signal. It shall also be possible to calculate the controlling feedback signal as the average of all feedback signals or the difference between a pair of feedback signals.

4.12	The VFD shall be able to apply individual scaling to each feedback signal.

4.13	For fan flow tracking applications, the VFD shall be able to calculate the square root of any or all individual feedback signals so that a pressure sensor can be used to measure air flow.

4.14	The VFD’s PID controller shall be able to actively adjust its setpoint based on flow. This allows the VFD to compensate for a pressure feedback sensor which is located near the output of the pump rather than out in the controlled system.

4.15	The VFD shall have three additional PID controllers which can be used to control damper and valve positioners in the system and to provide setpoint reset.

4.16	Floating point control interface shall be provided to increase/decrease speed in response to contact closures.

4.17	Five simultaneous meter displays shall be available. They shall be selectable from (at a minimum), frequency, motor current, motor voltage, VFD output power, VFD output energy, VFD temperature in degrees, feedback signals in their own units, among others.

4.18	Programmable Sleep Mode shall be able to stop the VFD. When its output frequency drops below set “sleep” level for a specified time, when an external contact commands that the VFD go into Sleep Mode, or when the VFD detects a no-flow situation, the VFD may be programmed to stop.  When the VFD’s speed is being controlled by its PID controller, it shall be possible to program a “wake-up” feedback value that will cause the VFD to start. To avoid excessive starting and stopping of the driven equipment, it shall be possible to program a minimum run time before sleep mode can be initiated and a minimum sleep time for the VFD.

4.19	A run permissive circuit shall be provided to accept a “system ready” signal to ensure that the VFD does not start until dampers or other auxiliary equipment are in the proper state for VFD operation. The run permissive circuit shall also be capable of initiating an output “run request” signal to indicate to the external equipment that the VFD has received a request to run.

4.20	VFD shall be programmable to display feedback signals in appropriate units, such as inches of water column (in-wg), pressure per square inch (psi) or temperature (°F). Examples can be room temperature in 0C , return air temperature in 0C , supply air temperature in 0C,  CO2 concentration in ppm, pressure in bar, differential pressure in PSI etc.

4.21	VFD shall be programmable to sense the loss of load. The VFD shall be programmable to signal this condition via a keypad warning, relay output and/or over the serial communications bus. To ensure against nuisance indications, this feature must be based on motor torque, not current, and must include a proof timer to keep brief periods of no load from falsely triggering this indication.

4.22	Standard Control and Monitoring Inputs and Outputs

4.22.1	Four dedicated, programmable digital inputs shall be provided for interfacing with the systems control and safety interlock circuitry.

4.22.2	Two terminals shall be programmable to act as either as digital outputs or additional digital inputs.

4.22.3	Two programmable relay outputs, Form C 240 V AC, 2 A, shall be provided for remote indication of VFD status.

4.22.4	Each relay shall have an adjustable on delay / off delay time.

4.22.5	Two programmable analog inputs shall be provided that can be either direct-or-reverse acting.

4.22.6	Each shall be independently selectable to be used with either an  analog voltage or current signal.

4.22.7	The maximum and minimum range of each shall be able to be independently scalable from 0 to 10 V dc and 0 to 20 mA.

4.22.8	A programmable low-pass filter for either or both of the analog inputs must be included to compensate for noise.

4.22.9	The VFD shall provide front panel meter displays programmable to show the value of each analog input signal for system set-up and troubleshooting,

4.22.10	One programmable analog current output (0/4 to 20 mA) shall be provided for indication of VFD status. This output shall be programmable to show the reference or feedback signal supplied to the VFD and for VFD output frequency, current and power. It shall be possible to scale the minimum and maximum values of this output.

4.22.11	It shall be possible to read the status of all analog and digital inputs of the VFD through serial bus communications.

4.22.12	It shall be possible to command all digital and analog output through the serial communication bus.

4.23	Optional Control and Monitoring Inputs and Outputs

4.23.1	It shall be possible to add optional modules to the VFD in the field to expand its analog and digital inputs and outputs.

4.23.2	These modules shall use rigid connectors to plug into the VFD’s control card.

4.23.3	The VFD shall automatically recognize the option module after it is powered up. There shall be no need to manually configure the module.

4.23.4	Modules may include such items as:

4.23.5	Additional digital outputs, including relay outputs

4.23.6	Additional digital inputs

4.23.7	Additional analog outputs

4.23.8	Additional analog inputs, including Ni or Pt temperature sensor inputs

4.23.9	It shall be possible through serial bus communications to control the status of all optional analog and digital outputs of the VFD.

4.24	Standard programmable firefighter’s override mode allows a digital input to control the VFD and override all other local or remote commands. It shall be possible to program the VFD so that it will ignore most normal VFD safety circuits including motor overload. The VFD shall display FIREMODE whenever in firefighter’s override mode.  Firemode shall allow selection of forward or reverse operation and the selection of a speed source or preset speed, as required to accommodate local fire codes, standards and conditions.

4.25	A real-time clock shall be an integral part of the VFD.

4.25.1	It shall be possible to use this to display the current date and time on the VFD’s display.

4.25.2	Ten programmable time periods, with individually selectable ON and OFF functions shall be available. The clock shall also be programmable to control start/stop functions, constant speeds, PID parameter setpoints and output relays. Is shall be possible to program unique events that occur only during normal work days, others that occur only on non-work days, and others that occur on specific days or dates. The manufacturer shall provide free PC-based software to set up the calendar for this schedule.

4.25.3	All VFD faults shall be time stamped to aid troubleshooting.

4.25.4	It shall be possible to program maintenance reminders based on date and time, VFD running hours, or VFD operating hours.

4.25.5	The real-time clock shall be able to time and date stamp all faults recorded in the VFD fault log.

4.25.6	The VFD shall be able to store load profile data to assist in analyzing the system demand and energy consumption over time.

4.25.6.1	The VFD shall include a sequential logic controller to provide advanced control interface capabilities. This shall include:

4.25.6.2	Comparators for comparing VFD analog values to programmed trigger values

4.25.6.3	Logic operators to combine up to three logic expressions using Boolean algebra

4.25.6.4	Delay timers

4.25.6.5	A 20-step programmable structure

4.26	The VFD shall include a Cascade Controller which allows the VFD to operate in closed loop set point (PID) control mode one motor at a controlled speed and control the operation of 3 additional constant speed motor starters.

5	SERIAL COMMUNICATIONS

5.1	The VFD shall include a standard EIA-485 communications port and capabilities to be connected to the following serial communication protocols at no additional cost and without a need to install any additional hardware or software in the VFD:

Metasys N2

Modbus RTU

5.2	VFD shall have standard USB port for direct connection of Personal Computer (PC) to the VFD. The manufacturer shall provide no-charge PC software to allow complete setup and access of the VFD and logs of VFD operation through the USB port. It shall be possible to communicate to the VFD through this USB port without interrupting VFD communications to the building management system.

5.3	The VFD shall have provisions for an optional 24 V DC back-up power interface to power the VFD’s control card. This is to allow the VFD to continue to communicate to the building automation system even if power to the VFD is lost.

6 	ADJUSTMENTS

6.1	The VFD shall have a manually adjustable carrier frequency that can be adjusted in 0.5 kHz increments to allow the user to select the desired operating characteristics. The VFD shall also be programmable to automatically reduce its carrier frequency to avoid tripping due to thermal loading.

6.2	Four independent setups shall be provided.

6.3	Four preset speeds per setup shall be provided for a total of 16.

6.4	Each setup shall have two programmable ramp up and ramp down times. Acceleration and deceleration ramp times shall be adjustable over the range from 1 to 3,600 seconds.

Each setup shall be programmable for a unique current limit value. If the output current from the VFD reaches this value, any further attempt to increase the current produced by the VFD will cause the VFD to reduce its output frequency to reduce the load on the VFD. If desired, it shall be possible to program a timer which will cause the VFD to trip off after a programmed time period.

If the VFD trips on one of the following conditions, the VFD shall be programmable for automatic or manual reset: external interlock, under-voltage, over-voltage, current limit, over temperature, and VFD overload.

The number of restart attempts shall be selectable from 0 through 20 or infinitely and the time between attempts shall be adjustable from 0 through 600 seconds.

An automatic “start delay” may be selected from 0 to 120 seconds. During this delay time, the VFD shall be programmable to either apply no voltage to the motor or apply a DC braking current if desired.

Four programmable critical frequency lockout ranges to prevent the VFD from operating the load at a speed that causes vibration in the driven equipment shall be provided.  Semi-automatic setting of lockout ranges shall simplify the set-up.

7 	OPTIONAL FEATURES

7.1 	All optional features shall be built and mounted by VFD manufacturer as an inbuilt factory solution. All optional features shall be UL listed by the VFD manufacturer as a complete assembly and carry a UL label.

8 	SERVICE CONDITIONS

8.1	Ambient temperature at full speed, full load operation with continuous drive rated output current:

8.2	-10 to 45°C  for ratings upto 90 kW without derating

8.2	-10 to 40°C for ratings 110 kW and higher without derating

8.3	Relative Humidity :  0 to 95%, non-condensing.

8.4	Elevation : Up to 3,300 feet without derating.

8.5	AC line voltage variation :  +  10% of nominal with full output.

8.6	VFD Enclosure protection : Minimum IP 55, integral, with no additional cabinets.

8.7	Side Clearances : No side clearance shall be required for cooling.

8.8	All power and control wiring shall be done from the bottom.

8.9	All VFDs shall be plenum rated.

9 	QUALITY ASSURANCE

9.1	To ensure quality, the complete VFD shall be tested by the manufacturer. The VFD shall drive a motor connected to a dynamometer at full load and speed and shall be cycled during the automated test procedure.

9.2	All optional features shall be functionally tested at the factory for proper operation.

# C.20	INSPECTION, TESTING AND COMMISSIONING

- INSPECTION AND TESTING

I.	All equipment and components supplied may be subjected to inspection and tests by the Owner/PMC-in-charge during manufacture, erection/installation and after completion. The inspection and tests shall include but not be limited by the requirements of this contract document. Prior to inspection and testing, the equipment shall undergo pre-service cleaning and protection.

III.	No tolerances shall be allowed other than the tolerances specified or permitted in the relevant approved Standards, unless otherwise stated.

IV.	If the guaranteed performance of any item of equipment is not met and / or if any item fails to comply with the specification requirement in any respect whatsoever at any stage of manufacture, test or erection, the Owner/PMC-in-charge may reject the item, or defective component thereof, whichever he considers necessary; and after adjustment or modification as directed by the Owner/PMC-in-charge, the contractor shall submit the item for further inspection and /or test.

V.	The approval of the Owner/PMC-in-charge of inspection and/or test results shall not prejudice the right of the Owner/PMC-in-charge to reject an item of equipment if it does not comply with the contract document when erected, does not or prove completely satisfactory in service.

VI.	The Contractor shall be responsible for the timely transmission of the relevant and appropriate sections of the contract document to manufacturers and sub-contractors for the proper execution of all tests at their works as per contract specifications.

- TESTS AT MANUFACTURER’S WORKS

I.	All tests to be performed during manufacture, fabrication and inspection shall be agreed with the Owner/PMC-in-charge prior to commencement of the work. The Contractor shall prepare the details of the schedule and submit these to the Owner/PMC-in-charge for approval. It must be ensured that adequate relevant information on the design code/standard employed, the manufacture /fabrication/assembly procedure and the attendant quality control steps proposed are made available to the Owner/PMC-in-charge who will mark in the appropriate spaces his intention to attend or waive the invited tests, or inspections.  Contractor shall arrange inspection and factory witness test for centrifugal, screw chiller and vapour absorption chiller.

II.	A minimum of twenty-one days’ notice of the readiness of equipment for test or inspection shall be provided to the Owner/PMC-in-charge  by the Contractor (whether the tests be held at the Contractors or Sub-contractor’s works). The subject items should remain available for Owner/PMC-in-charge inspection and test up to a minimum 10 days beyond the agreed date of witnessing the test. Every facility in respect of access, drawings, instruments and manpower shall be provided by the Contractor and sub-contractor to enable the Owner/PMC-in-charge to carry out the necessary inspection and testing of the Plant.

III.	No plant shall be packed, prepared for shipment, or dismantled for the purpose of packing for shipment, unless it has been satisfactorily inspected, all tests called for have been successfully carried out in the presence of the Owner/PMC-in-charge or approved for shipment, or alternatively inspection has been waived.

IV.	Functional electrical, mechanical and hydraulic tests shall be carried out on completed assemblies in the works. The extent of these tests and method of recording the results shall be submitted to, and agreed by, the Owner/PMC-in-charge in sufficient time to enable the tests to be satisfactorily witnesses, or if necessary for any changes required to the proposed programme of tests to be agreed.

V.	The Owner/PMC-in-charge reserves the right to visit the Manufacturer’s works at any reasonable time during fabrication of equipment and to familiarize himself with the progress made and the quantity of the work to date.

VI.	Within 30 days of completion of any tests, triplicate sets of all principal test records, test certificates and correction and performance curves shall be supplied to the Owner/PMC-in-charge.

VII.	These test records, certificates and performance curves shall be supplied for all tests, whether or not they have been witnessed by the Owner/PMC-in-charge or not. The information given on such test certificates and curves shall be sufficient to identify the material or equipment to which the certificate refers and should also bear the Contract reference title.

VIII.	When all equipment has been tested, the test certificates from all works and site tests shall be compiled by the Contractor into volumes and bound in an approved from complete with index and four copies of each volume shall be supplied to Owner/PMC-in-charge.

- PERFORMANCE TESTS AT MANUFACTURER’S WOKS

I.	All equipment may be subjected to routine performance tests at the Manufacturer’s Works in accordance with the relevant ANSI, ASME, ASTM, BIS standard including operating tests of complete assemblies to ensure correct operation of apparatus and components.

II.	Pumps, fans, compressor, and other rotating equipment shall be given full load tests, and run to 15% overspeed for 5 minutes to check vibration. Main and auxiliary gear boxes shall be subjected to shock load tests and a six-hour endurance run at rated speed and maximum torque.

III.	The Contractor shall submit single line diagrams including the layout of the Plant together with the location of test instrumentation and the principal dimensions of the layout. All calculations to derive performance data shall be made strictly in accordance with format given in the approved standards. Any alterations or deviations from the approved standard test layout or formulae shall be subjected to the prior approval of the Owner/PMC-in-charge.

IV.	The performance test shall be conducted over the full operating range of the pump to a closed valve condition and a minimum of five measurement points covering the full range shall be taken. Curves indicating Quality vs. Head, Quantity vs. Power absorbed, and Quantity vs. Pump efficiency shall be provided. In addition, a curve of the NPSH required vs. Quantity shall be provided except when the suction conditions do not require this test. Any proposal for the omission of this test shall be to the approval of the Owner/PMC-in-charge

V.	On completion of the tests the Contractor shall submit a report showing the test results obtained together with the curves corrected to the site operating conditions.

# C.21	TESTING, ADJUSTING AND BALANCING

1	SCOPE

a.	Testing, adjusting and balancing of heating, ventilating and air-conditioning systems at site.

b.	Testing, adjusting and balancing of HVAC Hydronic system at site.

c.	Testing, adjusting and balancing of exhaust system at site.

Comply with current editions of all applicable practices, codes, methods of standards prepared by technical societies and associations including:

ASHRAE	:	Latest HVAC Application.

SMACNA	:	Manual for the Balancing and Adjustment of air distribution

system.

2	PERFORMANCE

a.	Verify design conformity.

- Establish fluid flow rates, volumes and operating pressures.

- Take electrical power readings for each motor.

- Establish operating sound and vibration levels.

- Adjust and balance to design parameters.

- Record and report results as per the formats specified.

3	DEFINITIONS

- Test		:	To determine quantitative performance of equipment.

- Adjust		:	To regulate for specified fluid flow rates and air patterns at 				terminal equipment (e.g. reduce fan speed, throttling etc.)

- Balance		:	To proportion within distribution system (submains, branches 				and terminals) in accordance with design quantities.

4	TESTING, ADJUSTING AND BALANCING (TAB) PROCEDURES

The following procedures shall be directly followed in TAB of the total system.

Before commencement of each one of the TAB procedure explained hereunder, the contractor shall intimate the PMC about his readiness to conduct the TAB procedures in the format given in these specifications.

5	DESCRIPTION OF SYSTEM AND REQUIREMENTS

Adjust and balance the following system to provide most energy efficient operation compatible with selected operating conditions.

- All supply, return and outside air systems.

- All exhaust air systems.

- All chilled water systems.

- All cooling tower (condenser) water systems.

- Emergency purge systems.

6	AIR SYSTEMS

I.	Air Handlers Performance

The procedure shall establish the right selection and performance of the AHUs with the following results :

- Air-IN DB and WB temperature.

- Air-OUT DB and WB temperature.

- Dew point air leaving.

- Sensible heat flow.

- Latent heat flow.

- Sensible heat factor.

- Fan air volume.

- Fan air outlet velocity.

- Fan static pressure.

- Fan power consumption.

- Fan speed.

II.	Air distribution

Both supply and return air distribution for each AHU and for areas served by the AHU shall be determined and adjusted as necessary to provide design air quantities. It shall cover balancing of air through main and branch ducts utilising telescoping probes of      Electronic Rotating Vane Anemometers and Accubalance for grilles and diffusers.

III.	The Preparatory Work

To conduct the above test, following preparatory works are required to be carried out including the availability of approved for construction shop drawings and submittals :

- All outside air intake, return air  and exhaust air dampers are in proper position.

- All system volume dampers and fire dampers are in full open position.

- All access doors are installed & are air tight.

- Grilles are installed & dampers are fully open.

- Provision and accessibility of usage of TAB instruments for traverse measurements are available.

- All windows, doors are in position.

- Duct system are of proper construction and are equipped with turning vanes and joints are sealed.

h.	Test holes and plugs for ducting.

7	HYDRONIC SYSTEM BALANCING

- The Hydronic system shall involve the checking and balancing of all water pumps, piping network (main & branches), the heat exchange equipment like cooling and heating coils, condensers and chillers and cooling towers in order to provide design water flows.

II.	The essential preparation work, must be done by the contractor prior to actual testing, adjusting and balancing of HVAC system and ensure following :

- Availability of co-ordinated drawings and approved submittals and system sketch with design water flows specified thereon.

- Hydronic system is free of leaks,  is hydrostatically tested and is thoroughly cleaned, flushed and refilled.

- Hydronic system is vented.

III.	The contractor shall confirm completion of the basic procedures and prepare check lists for readiness of system balance.

- Check pumps operation for proper rotation and motor current drawn etc.

- Confirm that provisions for TAB measurements (Temperature, pressure and flow measurements) have been made.

- Open all shut-off valves and automatic control valves to provide full flow through coils. Set all balancing valves in the preset position, if these values are known. If not, shut all riser balancing valves except the one intended to be balanced first.

Balancing work for both Chilled Water System and Condenser Water System shall be carried out in a professional manner and test reports in the specified format shall be prepared and presented to the PMC/Consultants for approval.

8	READINESS FOR COMMENCEMENT OF TAB

Before starting of any of the tests, the readiness to do so should be recorded as per the prescribed check list.

9	TAB INSTRUMENTS

I.	Air Measuring Instruments

a.	For measuring DB and WB temperature, RH and dew point, microprocessor based TSI USA make VelociCalc Plus Meter, Model 8386, or equivalent shall be used.  This instrument shall be capable of calculating the sensible, latent  total heat flows, sensible heat factor and give printouts at site and have data logging/downloading facility.

b.	For measuring Air velocity, DB temperature and Air volume, TSI USA make  VelociCalc meter model 8386/ 8345 or equivalent shall be used. It shall be able to provide instant print out of recorded Air volume readings.

c.	Pitot tube.

d.	Electronic Rotary Vane Anemometer TSI make or equivalent.

e.	Accubalance Flow Measuring Hood TSI make or equivalent.

[All above instruments shall have a valid certification from a reputed testing institution.

II.	Hydronic Measuring Instruments

- For measurement of water flow across balancing valves, instruments as provided by the manufacturer of the valves specific to the type of valves shall be need.  This shall include but not be limited to differential pressure manometers.  Temperature shall be measured using electric thermometers from thermowells provided at strategic location by the HVAC contractor.

The water balancing shall be carried out being computer simulation program provided / certified by the balancing valve manufacturer.

III.	Rotation Measuring Instrument

- Electronic Digital Tachometer.

IV.	Temperature & RH Measuring Instrument

- TSI VelociCalc model 8386 / VelociCalc model 8345 or equivalent.

V.	Electrical Measuring Devices

- Clamp on Volt ammeter.

- Continuity Meter.

VI.	Vibration and Noise Levels

Vibration and alignment field measurements shall be taken for each circulating water pump, water chilling unit, air handling unit and fan driven by a motor over 10 HP. Readings shall include shaft alignment, equipment vibration, bearing housing vibration, and other test as directed by the Owner/PMC-in-charge.

Sound level readings shall be taken at ten (10) locations in the building as selected by the Owner/PMC-in-charge. The readings shall be taken on an Octave Band nalyzer in a manner acceptable to them. The contractor shall submit test equipment data and reporting forms for review. In order to reduce the ambient noise level, the readings shall be taken at night. All test shall be performed in the presence of Owner/PMC-in-charge.

SYSTEM READY TO BALANCE CHECK LIST

|  |  | Ready |  |  | Date |  |  | Ready |  | Date |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. HVAC Units (AHU) |  | Yes | No. |  | Corrected |  |  | Yes | No. | Corrected |
| a) General |  |  |  |  |  |  | e) Vibriation isolation |  |  |  |
| Louvers installed |  |  |  |  |  |  | Springs and compression |  |  |  |
| Manual dampers open & locked |  |  |  |  |  |  | Base level and free |  |  |  |
| Automatic dampers set properly |  |  |  |  |  |  |  |  |  |  |
| Housing Construction-leakage |  |  |  |  |  |  | 2. Duct systems |  |  |  |
| Access doors-leakage |  |  |  |  |  |  | a) General |  |  |  |
| Condensate drain piping and pan |  |  |  |  |  |  | Manual dampers open & locked |  |  |  |
| Free from dirt and debris |  |  |  |  |  |  | Access doors closed and tight |  |  |  |
| Nameplate data |  |  |  |  |  |  | Fire dampers open and accessible |  |  |  |
| b) Filters |  |  |  |  |  |  | Terminal units open and set |  |  |  |
| Type and size |  |  |  |  |  |  | Registers and diffusers open and set |  |  |  |
| Number |  |  |  |  |  |  | Turning vanes in square elbows |  |  |  |
| Clean |  |  |  |  |  |  | Provisions made for TAB measurements. |  |  |  |
| Frame-Leakage |  |  |  |  |  |  | Systems installed as per plans. |  |  |  |
| c) Coils (Hydronic) |  |  |  |  |  |  | Ductwork sealed as required |  |  |  |
| Size and rows |  |  |  |  |  |  | b) Architectural |  |  |  |
| Fin spacing and condition |  |  |  |  |  |  | Windows installed and closed. |  |  |  |
| Obstructions and / or debris |  |  |  |  |  |  | Doors closed as required. |  |  |  |
| Airflow and direction |  |  |  |  |  |  | Ceiling plenums installed and sealed. |  |  |  |
| Piping leakage |  |  |  |  |  |  | Access doors closed and tight |  |  |  |
| Correct piping Connections and flow |  |  |  |  |  |  | Air shafts and openings as required |  |  |  |
| Valves open or set |  |  |  |  |  |  |  |  |  |  |
| Airvents or steam traps |  |  |  |  |  |  | 3. Pumps. |  |  |  |
| Provisions made for TAB measurements |  |  |  |  |  |  | a) Motors. |  |  |  |
| d) Fans. |  |  |  |  |  |  | Rotation |  |  |  |
| Rotation. |  |  |  |  |  |  | Lubrication |  |  |  |
| Wheel clearance and balance |  |  |  |  |  |  | Alignment |  |  |  |
| Bearing and motor lubrication |  |  |  |  |  |  | Set screws tight |  |  |  |
| Drive alignment |  |  |  |  |  |  | Guards in place |  |  |  |
| Belt t tension. |  |  |  |  |  |  | Tank level and controls. |  |  |  |
| Drive set screws tight |  |  |  |  |  |  | Starters and disconnect switches |  |  |  |
| Belt guard in place |  |  |  |  |  |  | Electrical service & connections. |  |  |  |
| Flexible duct connector alignment |  |  |  |  |  |  | Nameplate data. |  |  |  |
| Starters and disconnect switches |  |  |  |  |  |  |  |  |  |  |
| Electrical service & connections. |  |  |  |  |  |  |  |  |  |  |
| Nameplate data |  |  |  |  |  |  |  |  |  |  |
| e) Piping |  |  |  |  |  |  | 5. Refrigeration Equipment |  |  |  |
| Correct flow |  |  |  |  |  |  | Crankcase heaters energized |  |  |  |
| Correct connections |  |  |  |  |  |  | Operating controls and devices. |  |  |  |
| Leakage |  |  |  |  |  |  | Safety controls and devices. |  |  |  |
| Valves open or set |  |  |  |  |  |  | Valves open |  |  |  |
| Strainer clean |  |  |  |  |  |  | Piping connections and flow |  |  |  |
| Air vented |  |  |  |  |  |  | Flexible connectors |  |  |  |
| Flexible connectors |  |  |  |  |  |  | Oil level and lubrication |  |  |  |
| Provisions made for TAB measurements |  |  |  |  |  |  | Alignment and drives. |  |  |  |
| f) Bases |  |  |  |  |  |  | Guards in place. |  |  |  |
| Vibration isolation. |  |  |  |  |  |  | Vibration isolation. |  |  |  |
| Grouting |  |  |  |  |  |  | Starters, contactors and disconnect switches. |  |  |  |
| Leveling. |  |  |  |  |  |  | Electrical connectors. |  |  |  |
|  |  |  |  |  |  |  | Nameplate data. |  |  |  |
| 2. Hydronic equipment. |  |  |  |  |  |  |  |  |  |  |
| a) Heat Exchangers/HW coil |  |  |  |  |  |  | 6. Hydronic Piping systems. |  |  |  |
| Correct flow and connections |  |  |  |  |  |  | Leak tested. |  |  |  |
| Valves open or set |  |  |  |  |  |  | Fluid levels and make-up |  |  |  |
| Airvents or steam traps |  |  |  |  |  |  | Relief or safety valves. |  |  |  |
| Leakage |  |  |  |  |  |  | Compression tanks and air vents. |  |  |  |
| Provisions made for TAB measurements |  |  |  |  |  |  | Steam traps and connections. |  |  |  |
| Nameplate data. |  |  |  |  |  |  | Strainers clean |  |  |  |
| b) Cooling towers |  |  |  |  |  |  | valves open or set |  |  |  |
| Correct flow and connections. |  |  |  |  |  |  | Provisions made for TAB measurements. |  |  |  |
| Valves open or set |  |  |  |  |  |  | Systems installed as per plans. |  |  |  |
| Leakage |  |  |  |  |  |  |  |  |  |  |
| Provisions made for TAB measurements |  |  |  |  |  |  | 7. Controls System |  |  |  |
| Sump water level. |  |  |  |  |  |  | Data centers. |  |  |  |
| Spray nozzles. |  |  |  |  |  |  | Outdoor return air reset |  |  |  |
| Fan/pump rotation. |  |  |  |  |  |  | Economizer |  |  |  |
| Motor/fan lubrication. |  |  |  |  |  |  | Static pressure |  |  |  |
| Drives and alignment |  |  |  |  |  |  | Room controls. |  |  |  |
| Guards in place. |  |  |  |  |  |  | 8. Other Checks. |  |  |  |
|  |  |  |  |  |  |  | a) Other trades or personnel notified of TAB work requirements. |  |  |  |
|  |  |  |  |  |  |  | b) Preliminary data complete |  |  |  |
|  |  |  |  |  |  |  | c) Test report forms prepared. |  |  |  |

INSTRUMENT CALIBRATION REPORT

PROJECT _____________________________________________________________________

| INSTRUMENT / SERIAL NO. | APPLICATION | DATES OF USE | CALIBRATION TEST DATE. |
| --- | --- | --- | --- |

REMARKS.

TEST  DATE _________________________READINGS BY ____________________________

CHILLER TEST REPORT

(TO BE FURNISHED BY INSTALLER)

PROJET _____________________________UNIT____________________________________

LOCATION____________________________________________________________________

MANUF.___________________ MODEL _______________SERIAL NO. __________________

CAPACITY ____________          REFRIG ___________        STARTER___________

HEATER SIZE ___________

| COMPRESSOR | DESIGN | ACTUAL |  | MOTOR STARTER | DESIGN | ACTUAL |
| --- | --- | --- | --- | --- | --- | --- |
| Make / Model |  |  |  | Make / Model |  |  |
| Serial No. |  |  |  | Type |  |  |
| Type (Centrifugal Sealedd, Semi Sealed, Screw Rotart) |  |  |  | Voltas |  |  |
| Piping Material |  |  |  | Amps |  |  |
| Suction Pr / Tem. |  |  |  | O/L Release Range |  |  |
| Discharge Pr/Temp |  |  |  |  |  |  |
| Refrigerant |  |  |  | EVAPORATOR | DESIGN | ACTUAL |
| Oil Pump Type |  |  |  | Make / Model |  |  |
| Oil Pressure |  |  |  | No. of Passes |  |  |
| Oil Failure Switch Pressure |  |  |  | Ref : Level |  |  |
| Unload Arrangement |  |  |  | Ref : Pressure / Temperature |  |  |
| Unload Set Points |  |  |  | Ent. Water Temp/Pressure |  |  |
| Drive |  |  |  | Leaving Water Temp/Pressure |  |  |
| Compressor Speed |  |  |  | Temperature Difference |  |  |
| Oil Level |  |  |  | Pressure Difference |  |  |
| Oil Temperature |  |  |  | Water Quantity CPM |  |  |
| L P Setting |  |  |  | Relief Valve Setting |  |  |
| H P Setting |  |  |  | IKW / Ton |  |  |
| Anti Freeze Setting |  |  |  |  |  |  |
| Purge Unit Type |  |  |  |  |  |  |
| Purge Operation Checked |  |  |  | CONDENSER | DESIGN | ACTUAL |
|  |  |  |  | Make/Model |  |  |
|  |  |  |  | No. of Passes |  |  |
|  |  |  |  | Ref : Pressure / Temp |  |  |
| COMPRESSOR MOTOR | DESIGN | ACTUAL |  | Ent. Water Temp / Pressure |  |  |
| Make / Model |  |  |  | Leaving Water Temp/Pressure |  |  |
| Type |  |  |  | Temperature Difference |  |  |
| Voltage I1 Ie I2 I3 I3 I1 |  |  |  | Pressure Difference |  |  |
| Motor Rated Current |  |  |  | Water Quantity CPM |  |  |
| Motor F L Current |  |  |  | Relief Valve Setting |  |  |

REMARKS

TEST DATE _________________________READINGS BY ______________________________

PUMP TEST REPORT

PROJECT _______________________________________________

| DATA | PUMP NO. | PUMP NO. | PUMP NO. | PUMP NO. | PUMP NO. |
| --- | --- | --- | --- | --- | --- |
| Location |  |  |  |  |  |
| Service |  |  |  |  |  |
| Manufacturer |  |  |  |  |  |
| Model Number |  |  |  |  |  |
| Serial Number |  |  |  |  |  |
| GPM/Head |  |  |  |  |  |
| Req. NPSH |  |  |  |  |  |
| Pump RPM |  |  |  |  |  |
| Impeller Diam. |  |  |  |  |  |
| Motor Mfr. / Frame |  |  |  |  |  |
| Motor HP/RPM |  |  |  |  |  |
| Volts/Phase/Hertz |  |  |  |  |  |
| F.L Amps |  |  |  |  |  |
| Seal Type |  |  |  |  |  |
| Pump Off-Press. |  |  |  |  |  |
| Valve Shut Diff. |  |  |  |  |  |
| Act.Impeller Diam. |  |  |  |  |  |
| Valve Open diff. |  |  |  |  |  |
| Valve Open GPM |  |  |  |  |  |
| Final Dischg. Press. |  |  |  |  |  |
| Final Suction Press. |  |  |  |  |  |
| Final Ap |  |  |  |  |  |
| Final GPM |  |  |  |  |  |
| Voltage T1 T2 T2 T3 T3 T1 |  |  |  |  |  |
| Amperage T1 T2 T3 |  |  |  |  |  |

REMARKS

TEST   DATE _____________________  	READINGS BY __________________________

COOLING TOWER TEST REPORT

PROJECT___________________________SYSTEM__________________________________

LOCATION___________________________________________________________________

MANUF.__________________ MODEL__________________SERIAL NO._________________

NOM. CAPACITY____________________________WATER TREAT._____________________

| COOLING TOWER / MOTOR / WATER DATA |  |  |  | AIR DATA | DESIGN | ACTUAL |
| --- | --- | --- | --- | --- | --- | --- |
| Make / Model |  |  |  | Fan CFM |  |  |
| Type |  |  |  | Outlet S.P. |  |  |
| Tons |  |  |  | Avg. Ent. W.B. |  |  |
| No. of Fan Motors |  |  |  | Avg. Lvg. W.B. |  |  |
| Motor HP / RPM |  |  |  | Ambient W.B. |  |  |
| Motor / Drive |  |  |  | Fan RPM |  |  |
| Motor Speed |  |  |  | Voltage I1 Ie I2 I3 I3 I1 |  |  |
| Motor Rated Current |  |  |  | Amps T1 Te T21 |  |  |
| Motor FL Current |  |  |  |  |  |  |
| O/L Release Setting |  |  |  |  |  |  |
| CT Range |  |  |  |  |  |  |
| CT Approach |  |  |  |  |  |  |
| COOLING TOWER FAN / AIR DATA | DESIGN | ACTUAL |  | WATER DATA | DESIGN | ACTUAL |
| No. of Fans |  |  |  | Ent//Lvg./Water Pressure |  |  |
| Type/ Drive of Fan |  |  |  | Ent//Lvg./Water Temperature |  |  |
| Fan Dia |  |  |  | Water Temperature – T |  |  |
| Fan Speed |  |  |  | GPM |  |  |
| Air Inlet Temperature |  |  |  | Bleed GPM |  |  |
| Air Outlet Temperature |  |  |  | Voltage I1 Ie I2 I3 I3 I1 |  |  |
| Fan Air Quantity |  |  |  | Amps T1 Te T21 |  |  |
| Water Bleed GPM |  |  |  |  |  |  |

REMARKS

TEST   DATE _____________________READINGS BY____________________________

AIR HANDLING EQUIPMENT TEST REPORT

PROJECT____________________________ SYSTEM / UNIT________________________

LOCATION_________________________________________________________________

| UNIT | DATA |  | MOTOR | DATA |
| --- | --- | --- | --- | --- |
| Make/Model No. |  |  | Make / Frame |  |
| Type/Size |  |  | H.P / RPM |  |
| Serial Number |  |  | Volts/Phase/cycles |  |
| Arr./Class |  |  | F.L amps. |  |
| Discharge |  |  | Pully Diam/Bore |  |
| Pully diam/Bore |  |  | Pully /Distance. |  |
| No. Belts/make/size |  |  |  |  |
| No.Filters/type.size (Pre.) |  |  |  |  |
| No.Filters/type/size (secondary) |  |  |  |  |

| TEST DATA | DESIGN | ACTUAL |  | TEST DATA | DESIGN | ACTUAL |
| --- | --- | --- | --- | --- | --- | --- |
| Total Cfm |  |  |  | Discharge S.P |  |  |
| Total S.P |  |  |  |  |  |  |
| Fan RPM |  |  |  | Cooling Coil S.P |  |  |
| Motor Volts. T1 T2 T2 T3 T3 T1 |  |  |  | Filters S.P |  |  |
| Outside air Cfm |  |  |  |  |  |  |
| Return air Cfm |  |  |  |  |  |  |

REMARKS.

TEST DATE____________________________ READINGS BY _________________________

COOLING / HEATING TEST REPORT (AHU)

PROJECT ___________________________________________________________________

| COIL DATA | COIL NO. | COIL NO. | COIL NO. | COIL NO. |
| --- | --- | --- | --- | --- |
| System Number |  |  |  |  |
| Location |  |  |  |  |
| Coil Type |  |  |  |  |
| No. Rows Fins/In |  |  |  |  |
| Manufacturer |  |  |  |  |
| Model Number |  |  |  |  |
| Face Area, Sq.Ft. |  |  |  |  |

| TEST DATA | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Air Qty. CFM |  |  |  |  |  |  |  |  |
| Air Vel.FPM |  |  |  |  |  |  |  |  |
| Press.Drop In. |  |  |  |  |  |  |  |  |
| Out.Air DB/WB |  |  |  |  |  |  |  |  |
| Ret. Air DB/WB |  |  |  |  |  |  |  |  |
| Ent.Air DB/WB |  |  |  |  |  |  |  |  |
| Lvg.Air DB/WB |  |  |  |  |  |  |  |  |
| Air AT |  |  |  |  |  |  |  |  |
| Waer flow. GPM |  |  |  |  |  |  |  |  |
| Press.Drop.PSI |  |  |  |  |  |  |  |  |
| Ent.Water Temp |  |  |  |  |  |  |  |  |
| Lvg .Water Temp |  |  |  |  |  |  |  |  |
| Water AT |  |  |  |  |  |  |  |  |
| Exp.Valve/Refrig |  |  |  |  |  |  |  |  |
| Refrig.Suction Pr. |  |  |  |  |  |  |  |  |
| Refrig.Suct.Temp |  |  |  |  |  |  |  |  |
| Inlet Steam press. |  |  |  |  |  |  |  |  |

REMARKS.

TEST DATE _________________________READINGS BY ___________________________

AIR COOLED HEAT PUMP

PROJECT____________________________  	SYSTEM__________________________________

LOCATION_________________________________________________________________________

| HOT WATER GENERATOR |  |  |  | HOT WATER PUMP MOTOR | DESIGN | ACTUAL |
| --- | --- | --- | --- | --- | --- | --- |
| Make / Model |  |  |  | Motor Make / Model |  |  |
| Type |  |  |  | Type |  |  |
| Capacity KW |  |  |  | Motor Speed |  |  |
| Volts |  |  |  | Motor Drive |  |  |
| No. of Steps |  |  |  | Motor Voltage |  |  |
| Power Supply |  |  |  | F L Current |  |  |
| F L Current |  |  |  | O / L Release Size |  |  |
| No. of Thermostat Steps |  |  |  |  |  |  |
| Water Inlet Temp./Pressure |  |  |  |  |  |  |
| Water Outlet Temp./Pressure |  |  |  |  |  |  |
| COOLING TOWER FAN / AIR DATA | DESIGN | ACTUAL |  | WATER DATA | DESIGN | ACTUAL |
| Make |  |  |  | Make / Model |  |  |
| Type |  |  |  | Type |  |  |
| Pump Pressure Inlet |  |  |  | Steam Pressure |  |  |
| Pump Pressure Outlet |  |  |  | Water Inlet Temp / Pressure |  |  |
| Pump Water Qty. |  |  |  | Water Outlet Temp / Pressure |  |  |
| Pump Drive / Speed |  |  |  | Water Qty. GPM |  |  |
|  |  |  |  | Water Temp |  |  |
|  |  |  |  | Water Pressure |  |  |

REMARKS

TEST   DATE ___________________  	READINGS BY __________________________

FAN COIL TEST REPORT

PROJECT____________________________________________DATE__________________

LOCATION__________________________________________________________________

MANUFACTURER____________________________________________________________

| AREA SERVED | FCU MAKE | CAPACITY TR | TEMPERATURE DEG. F |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | GRILLE | ROOM |  |

REMARKS.

TEST  DATE ____________________________   READINGS BY ___________________________

FAN TEST REPORT

PROJECT__________________________________________________________________

| FAN DATA | FAN NO. | FAN NO. | FAN NO. |
| --- | --- | --- | --- |
| Location |  |  |  |
| Service |  |  |  |
| Manufacturer |  |  |  |
| Model No. |  |  |  |
| Serial No. |  |  |  |
| Type / Class |  |  |  |
| Motor Make / Style |  |  |  |
| Motor H.P/RPM/ Frame |  |  |  |
| Volts/Phase/Cycles |  |  |  |
| F.L Amps. |  |  |  |
| Motor pully Diam./Bore |  |  |  |
| Fan pully Diam./Bore |  |  |  |
| No. Belts/ Make/Size |  |  |  |
| Pully Distance. |  |  |  |

| TEST DATA | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL |
| --- | --- | --- | --- | --- | --- | --- |
| CFM |  |  |  |  |  |  |
| FAN RPM |  |  |  |  |  |  |
| S.P IN/OUT |  |  |  |  |  |  |
| TOTAL S.P |  |  |  |  |  |  |
| Voltage T1 T2 T2 T3 T3 T1 |  |  |  |  |  |  |
| Amperage T1 T2 T3 |  |  |  |  |  |  |

REMARKS:

TEST DATE:_____________________________READINGS BY _____________________

RECTANGULAR DUCT

TRAVERSE REPORT

PROJECT__________________________SYSTEM________________________________

LOCATION / ZONE_____________________ACTUAL AIR TEMP. ________________

DUCT S.P_________

| DUCT SIZE__________SQ.FT.__________________ | REQUIRED FPM_______________CFM_______________ | ACTUAL FPM______________CFM_______________ |
| --- | --- | --- |

| POSITION | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 10 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 11 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 12 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 13 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| VEL1OCITY SUBTOTALS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

REMARKS.

TEST  DATE__________________________ READINGS BY ____________________________

GRILLES AND DIFFUSERS

TEST REPORT.

PROJECT_______________________________SYSTEM_________________________________

OUTLET MANUFACTURER____________________________

TEST  APPARATUS___________________

| AREA | OUT LET |  |  | DESIGN |  |  | PRLIMINARY |  |  |  |  | FINAL |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SERVED | NO. | TYPE | SIZE | CFM | VEL | VELOR CFM |  | VEL.OR CFM |  |  |  |  | VEL | CFM |  |  |

REMARKS.

TEST  DATE______________________  READINGS BY _________________________

# C.22	PAINTING AND FINISHES

19.1	SCOPE

The scope of this section comprises of design, supply and apply of colour scheme required for each piece of equipment

19.2	COLOUR SCHEME.

| - Description | Standard Colour & Reference | Lettering Colouring |
| --- | --- | --- |

| Exposed Duct Work (other than plant room) instruction | As per approval of Owner/PMC-in-charge |  |
| --- | --- | --- |
| Air Conditioning Duct Work (Plant Rooms) | BSS 111 Pale Blue | Black |
| Ventilation Duct Duct Work (Plant Rooms) | BSS 111 Pale Blue | Black |
| Conditioner Casings, Air Handling Units, Filter Plenums | BSS 111 Pale Blue | Black |
| Electrical (Conduit Ducts and Motors ) | BSS 557 Light Orange | Black |
| Chilled Water Pipe | Jade Green | Black |
| Drains | Black | White |
| Vents | White | Black |
| Fans | BSS 111 Pale Blue | Black |
| Valves and Pipe Line Fittings | White with black handles | Black |
| Beltquards | Black and yellow diagonal stripes (45 25 mm wide) |  |
| Switchboards - exterior - interior | As per approval of Owner/PMC-in-charge |  |
| Machine Bases, Inertia Bases and Plinths | Charcoal Grey |  |

# C.23	IDENTIFICATION OF SERVICES

1	SCOPE

The scope of this section comprises of identification of services for each piece of equipment and apply as mentioned in specifications below.

2	VALVE LABELS AND CHARTS

Each valve shall be provided with a label indicating the service being controlled, together with a reference number corresponding with that shown on the Valve Charts and “ as fitted” drawings.  The labels shall be made from 3 ply ( black / white/ black) Traffolyte material showing white letters and figures on a black background.  Labels to be tied to each valve with chromium plated linked chain.

A wall mounted, glass covered plan to the approval of the Architect / Owner/PMC shall be provided and desplayed in each plant room showing the plant layout with pipe work, valve diagram and valve schedule indicating size, service, duty, etc.

3	IDENTIFICATION OF SERVICES.

Pipe work and duct work shall be identified by colour bands 150 mm. wide or colour triangles of at least 150 mm. / side.  The bands of triangles shall be applied at termination points, junctions, entries and exits of plant rooms, walls and ducts, and control points to readily identify the service, but spacing shall not exceed 4.0 metres.

3.1.	Pipe work Services :-

For pipe work services and its insulation the colours of the bands shall comply with BS. 1710: 1971.

Basic colours for pipe line  identification :

| Pipe Line Contents | BS. 4800 Colour Reference | Colour. |
| --- | --- | --- |
| Water | 12 D 45 | Green |
| Steam | 10 A 03 | Grey |
| Oils | 06 C 39 | Brown |
| Gas | 08 C 35 | Yellow / Brown |
| Air | 20 E 51 | Blue |
| Drainage | 00 E 53 | Black |
| Electrical | 06 E 51 | Orange |

Colour code indicator bands shall be applied as colour bands over the basic identification colour in the various combinations as listed below :-

| Pipe Line Contents | Colour Bands to BS. 4800 |
| --- | --- |

| Water Services : |  |
| --- | --- |
| Cooling | 00 E 55 |
| Fresh / drinking | 18 E 53 |
| Boiler feed | 04 D 45/00 E 55 / 04 D 45 |
| Condensate | 04 D 45/14 E 53 / 04 D 45 |
| Chilled | 00 D 55/14 E 53 / 00 D 45 |

| Central Heating Services : |  |
| --- | --- |
| Below 100o C | 18 E 55/04 D 45/18 E 53 |
| Above 100o C | 04 D 45/18 E 53 /04 D 45 |

| Cold Water Storage Tanks : | 00 E 55/18 E 53/00 E 55 |
| --- | --- |
| Hot Water Supply | 00 E 55/04 D 45/00 E 55 |
| Hydraulic Power | 04 C 33 |
| Sea / River Untreated | Basic Colour only |
| Fire Extinguishing | 04 E 53 |
| Steam Services : | Basic Colour only |
| Air : Compressed Vacuum | Basic Colour only White. |
| Town Gas : Manufactured Natural | 14 E 53 10 E 53 |
| Oils : |  |
| Diesel | 00 E 55 |
| Lubricating | 14 E 53 |
| Hydraulic Power | 04 C 53 |
| Transformer | 04 D 45 |

| Drainage and other fluids : | Basic Colour only |
| --- | --- |
| Electrical Services : | Basic Colour only |

In addition to the colour bands specified above all pipe work shall be legibly marked with black or white letters to indicate the type of service and the direction of flow, identified as follows :-

| High Temperature Hot Water | HTHW |
| --- | --- |
| Medium Temperature Hot Water | MTHW |
| Low Temperature Hot Water | LTHW |
| Chilled Water | CHW |
| Condenser Water | CONDW |
| Steam | ST |
| Condensate | CN |

Pipe shall have the letters F and R added to indicate flow and return respectively as well as directional arrows.

3.2	Duct Work Services :

For Duct work  services and its insulation the colours of the triangles shall comply with BS.1710 : 1971.  The size of the symbol will depend on the size of the duct and the viewing distance but the minimum size should not be less than 150 mm. length per side.  One apex of the triangle shall point in the direction of airflow.

| - Services | Colour | BS.4800 Colour Reference |
| --- | --- | --- |
| Conditioned Air | Red and Blue | 04 E 53 / 18 E 53 |
| Ward Air | Yellow | 10 E 53 |
| Fresh Air | Green | 14 E 53 |

| Exhaust / Extract / Recirculated Air | Grey | AA 0 09 |
| --- | --- | --- |
| Foul Air | Brown | 06 C 39 |
| Dual Duct System Hot Supply Air | Red | 04 E 53 |
| Cold Supply Air | Blue | 18 E 53 |

In addition to the colour triangles specified above all duct work shall be legibly marked with black or white letters to indicate the type of service, identified as follows :-

| Supply Air | S |
| --- | --- |
| Return Air | R |
| Fresh Air | F |
| Exhaust Air | E |

The colour banding and triangles shall be manufactured from self-adhesive cellulose tape, laminated with a layer of transparent ethyl cellulose tape.

# C.24	NOISE CONTROL

1	SCOPE

The scope of this section comprises of the design, supply, installation, testing and commissioning of noise and vibration control equipment and accessories.

2		STANDARDS

The testing of all noise control equipment and the methods used in measuring the noise rating of air conditioning plant and equipment shall be in accordance with the relevant sections of the following British Standards, unless otherwise stated :

| BS 4718 : 1971 | Methods of Test of Silencers for Air Distribution Systems. |
| --- | --- |
| BS 2750 : Parts 1-9:1980 | Laboratory and Field Measurement of Airborne Sound Insulation of Various Building Elements. Recommendations for Field Laboratory Measurement of Airborne and Impact Sound Transmission in Buildings. |
| BS 3638 : 1987 | Methods of Measurement of Sound Adsorption in a Reverberation Room. |
| BS 4773 : Part 2: 1976 | Acoustic Testing. |
| BS 4856 : Part 2: 1976 | Acoustic performance without additional ducting of forced fan convection equipment. |
| Part 5: 1976 | Acoustic performance with additional ducting of forced fan convection equipment. |
| BS 4857 : Par 2:1978 (1983) | Acoustic Testing and Rating of High Pressure Terminal Reheat Units. |
| BS 4954 : Par 2:1978 (1987) | Acoustic Testing and Rating of Induction Units. |
| BS 5643 : 1984 | Glossary of Refrigeration, Heating, Ventilating and Air Conditioning Terms. |

3		GENERAL

Mechanical services shall generally be designed and installed with provisions to contain noise and the transmission of vibration, generated by moving plant and equipment at source where illustrated on the tender drawings and plant and equipment schedules to achieve acceptable noise rating specified for occupied areas.

In addition to the provisions specified in the Specification, particular attention must be given to the following details at time of ordering plant and equipment and their installation :-

a.	All moving plant , machinery and apparatus shall be statically and dynamically balanced at manufacturers works and certificates issued.

b.	The isolation of moving plant, machinery and apparatus including lines equipment from the building structure.

c.	Where duct work and pipe work services pass through walls, floors and ceilings, or where supported shall be surrounded with a resilient acoustic absorbing material to prevent contact with the structure and minimise the outbreak of noise from plant rooms.

d.  	The reduction of noise breakout from plant rooms and the selection of externally mounted equipment and plant to meet ambient noise level requirements of  the Specifications.

e.	Electrical conduits and connections to all moving plant and equipment shall be carried out in flexible conduit and cables to prevent the transmission of vibration to the structure and nullify the provisions of anti-vibration mountings.

f.	All duct connections to fans shall incorporate flexible connections, except in cases where these are fitted integral within air handling units.

Duct work connections to the fan inlets / outlets shall be concentricity aligned so that the flexible connections are not subjected to any strain and not used as a means of correcting bas misalignment.

g.	All resilient acoustic absorbing materials shall be non flammable, vermin and rot proof and shall not tend to break up or compress sufficiently to transmit vibration or noise from the equipment to the structure.

h.	Where practicable, silencers shall be built into walls and floors to prevent the flanking of noise the duct work systems and their penetrations sealed in the manner previously described.

Where this is not feasible, the exposed surface of the duct work between the silencer and the wall subjected to noise infiltration shall be acoustically clad as specified.

i.	Contractor to demonstrate design NC levels in the areas with FFT (Fast Fourier Transform) analyser.

4	SILENCERS

All silencers mentioned in the specification shall be selected based on preliminary sound power levels obtained from fan/air handling unit manufacturers or fan duties to achieve a noise rating in the occupied space and as per approval of Owner/PMC-in-charge.

All plant attenuators shall be selected to maintain noise criteria given in this Specification.

Attenuators shall be constructed from high quality pre-galvanised steel sheet casings with lock formed joints along the casing length.  Angle iron cross jointing flanges shall be fitted to silencer casings, drilled as required and finished with zinc cromet primer paint.

Acoustic splitters shall be formed by chancel section pre-galvanised sheet steel framework retaining acoustic fill of a density to attain the required performance.  Splitters shall have round nose ends to give smooth entry and exit conditions to minimise air pressure drops.

The acoustic fill shall be protected from the air flow by 22 swg minimum perforated galvanised sheet steel.

All silencers shall be selected against a maximum allowable air pressure drop of 75 a.

It will be the responsibility of the Contractor at the time of placing orders for fan equipment to obtain from the manufacturers, certified sound power levels to enable the selected duct silencers to be checked against the original design information, prior to orders being placed.

5	ANTI-VIBRATION MOUNTINGS.

All items of rotating and reciprocating plant and equipment  shall be isolated from the structure by the use of anti-vibration materials, mountings or spring loaded supports fixed to either concrete bases, inertia blocks or support steels as indicated.

Centrifugal fans and motors within air handling units shall be isolated from the frame of the air handling unit by suitable anti-vibration mountings.  Fan discharge air connections shall be fitted with approved flexible connections internally isolating the fan scroll from the air handling unit casing.

Axial flow fans shall be mounted on steel legs as diaphragm plates supported on neoprene in shear anti-vibration mountings, or suspended using spring loaded hangers to suite the application.

Centrifugal pumps shall be mounted on inertia bases consisting of reinforced concrete sub-base, anti-vibration mountings and concrete filled steel upper plinth.  The Contractor shall be responsible for issuing the steel upper plinth and mountings to the Contractor for building-in.

Pipe work connections to circulating pumps, chillers, cooler coils and other equipment shall be made with flexible connections as per Specifications.

The construction of the anti-vibration mountings shall generally comply with the  following: -

Enclosed Spring Mounting ( Caged or Restrained Springs)

Each mounting shall consist of cast or fabricated telescopic top and bottom housing enclosing one or more helical steel springs as the principle isolation elements, and shall incorporate a built- in levelling device.

The springs shall have an outside diameter of not less than 75% of the operating height, and be selected to have at least 50% overload capacity before becoming coil bound.

The bottom plate of each mounting shall have bonded to it a neoprene pad designed to attenuate any high frequency energy transmitted by the springs.

Mountings incorporating snubbers of restraining devices shall be designed so that the snubbing damping or restraining mechanism, is capable f being adjusted to have no significant effect during the normal running of the isolated machine.

Restrained isolator shall be provided on chillers subject to approval by the manufacturers.

6	OPEN SPRING MOUNTINGS.

Each mounting shall consist of one or more helical steel springs as the principal isolation elements, and shall incorporate a built-in leveling device.  The spring shall be fixed or otherwise securely located to cast or fabricated top and bottom plates, and shall have an outside diameter of not less than 75% of the operating height, and shall be selected to have at least 50% overload capacity before becoming coil-bound.

The bottom plate shall have bonded to it a neoprene pad designed to attenuate any high frequency energy transmitted by the springs.

7	NEOPRENE-IN-SHEAR MOUNTINGS.

Each mounting shall consist of a steel top plate and base plate completely embedded in oil resistant neoprene.  Each mounting shall be capable of being fitted with a levelling device, and bolt holes in the base plate and tapped holes in the top plate so that they may be bolted to the floor and equipment where required.

8	INERTIA BASES FOR PUMPS.

The inertia base shall be an all welded mild steel channel frame the minimum depth of which shall be 1/12  of the longest span between isolator but not less than 150 mm. filled with concrete the density of which shall be 2300 kg/m3.

The inertia base shall be sufficiently large to provide support for all parts of the equipment, including any component which overhang the equipment base, such as suction and discharge elbows on centrifugal pumps.

The frame shall include pre-located equipment anchor bolts fixed into position and housed in a steel sleeve allowing minor bolt location adjustment.

Isolator support brackets shall be welded into the corners of the base and suitably re-enforced for the load of the equipment and base.

Additional reinforcing roads shall be provided at 200 mm. centres to ensure the concrete and frame is adequately stiffened against distortion.

9	FLEXIBLE CONNECTIONS

Flexible connections shall be provided on all duct work connections to fans, rotating plant and equipment isolated from structure and anti-vibration materials or mountings.  Pipe work and duct work crossing building movement or construction joints shall be installed with flexible connections.

Flexible connections on duct work to fans etc., shall be a minimum / maximum free length of 100 mm. / 200 mm. respectively to minimise noise transmission and noise breakout.  They shall be completely free from stress and shall not be required to accept any weight.

Thickness and strength of flexible connection materials shall be suitable to withstand the positive and negative fan pressures to which they will be subjected to and shall not allow perceptible leakage.  The materials shall be durable, non flammable having food acoustical quality.

Flexible connections shall be fitted to all pump suction and discharge connections, chillers and other vibrating equipment and where anti-vibration mounts and inertia basis are fitted.

Flexible connections shall be fitted to all cooler coil chilled water pipe work connections.

Flexible connections shall allow freedom of movement of plant in all plans.

Making flanges to pipe work flexible connections shall be of the smooth faced weld-nick type.

Rubber Bellows shall be fitted as close to the source of vibration at practicable.  The pipe at the other end of the bellows shall be a fixed point.

Rubber bellows shall be single convolution of multiply reinforced EPDM rubber with wire reinforced cuffs.  Flanges shall be able to swivel and be removable. The date of manufacture shall be moulded on the bellows. For traceability membranes shall have an indelible identification showing manufacturer, country of origin, the type and a batch number.

Tie bars with rubber top hat washers shall be used on bellows.

For working temperatures up to 70o C the rubber bellows shall be high tensile synthetic fibre reinforced.

For working temperature between 70oC and 100oC the bellows carcase shall be steel wire mesh reinforced throughout.  Steel reinforced bellows shall be manufactured and approved to the Standards.

For temperatures above 100oC bellow shall be multiply stainless steel with Van Stone ends swivel flanges.  The overall length shall not exceed 130 mm.

Flexible connections with screwed connections shall be reinforced EPDM rubber hoses and shall have at least one full union to avoid torturing on installation.

Flexible pipe connections on chilled water systems shall be suitable for a working pressure of 10 bar and test pressure of 17 bar.

# C.25	CHEMICAL (WATER) TREATMENT

1.	Scope

Design, Supply, installation, testing & commissioning of basic mechanical materials indicated as per approved Drawings and where required for the proper operation of the MEP systems.

For chilled water system, install water treatment system incorporating a manual feed dosing pot for chemicals (rust inhibitors and biocides) necessary for testing, commissioning and operation.  A specialized professional company, shall be appointed by the Contractor for the water treatment system.

2.	Submittals

Submit detail shop drawings for the system for approval.

Submit Raw Water Analysis from site to include the following information:

  - pH

  - Total Alkalinity

  - Chlorides

  - Silica

  - Hardness

  - Total dissolved solids

  - Submit the following:

  - System installation drawings and diagrams.

  - Product Information Sheets on each component, device pump controller, valve, etc., being supplied for the systems.

  - Product Information Sheets and Material Safety Data Sheets on all chemical products being supplied.

  - Recommended feed rates on each chemical product.

  - Recommended operating conditions for each system including cycles of concentration, chemical test limits of Water Treatment system set points.

3.	Operation and Maintenance Data

Submit operation and maintenance data.

Include data on chemical feed pumps, agitators, and other equipment including spare parts lists, procedures, and treatment programs.

Include step by step instructions on test procedures including target concentrations.

4.	Qualifications

Manufacturer: Company specializing in manufacturing the products specified in this Section with minimum ten years documented experience. Company shall have local representatives with water analysis laboratories and full time service personnel.

The water treatment company shall meet the following minimum requirements:

It shall be regularly engaged in this type of work and service and shall have a specialist with at least five years experience in the cleaning and chemical treatment of systems of similar size capacity, and shall be in active responsible charge of all treatment work.

It shall either operate or have access to a laboratory equipped to analyze samples in accordance with the standard methods of the American Water Works Association and the American Society for Testing Materials.

5.	Regulatory Requirements

Conform to applicable code for addition of non-potable chemicals to building mechanical systems, and for delivery to public sewage systems.

Conform to standards of ASHRAE, AWWA, ASTM and EPA

6.	Maintenance Service

Furnish service and maintenance of treatment systems for one year from Date of Substantial Completion as specified below for following systems:

7.	Cooling Towers (Condenser Water System)

Chilled Water System

Service

The Water Treatment company shall include start-up of chemical treatment and provide ongoing supervisory service through a minimum of monthly visits during the operating season to monitor the progress of the treatment program. Additional duties include training of Owner/PMC staff in the performance and interpretation of control tests and furnishing laboratory check analysis and reports on treated systems. Building staff shall be responsible for applying chemicals.  Service shall be provided for a period from start-up to Defect Liability Period. The Water Treatment firm shall be responsible for applying chemicals, adjusting bleed/blown down equipment and furnishing laboratory analysis for a period from start-up to Defect Liability Period. Schedule of service visits shall be as follows.

Cooling Towers (Condenser Water) Systems – Weekly

Chilled Water Systems – Monthly

Provide service and all required chemicals for initial cleaning, test equipment and all chemicals required from start-up to Defect Liability Period. Provide laboratory and technical assistance services for the service period.

All service visits shall be confirmed in writing to the Owner/PMC so that a complete record of service activities is available for examination by the Owner/PMC and the Owner/PMC. Submit two copies of each report.

Include eight-hour training course for operating personnel, instructing them on installation, care, maintenance, testing, and operation of water treatment systems. Arrange course at startup of systems at the job site.

Provide onsite inspections of equipment during scheduled or emergency shutdown to properly evaluate success of water treatment program, and make recommendations in writing based upon these inspections.

Legionella Pneumophilia Screening Tests shall be made on the cooling tower system a minimum of four times per year during the operating season. This test shall be performed by a qualified laboratory using Direct Florescent Antibody technique.  The laboratory report shall state the number of Legionella Pneumophilia bacteria per millilitre. Reports shall be forwarded to the Owner/PMC. The water treatment program shall be adjusted if necessary based on the test results.

Carry out 30-day and 90-day tests of coupon racks to determine corrosion rate.  Reports shall be forwarded to the Owner/PMC.

8.	Maintenance Manuals

Submit maintenance materials for all the systems mentioned above.

Provide sufficient chemicals for treatment and testing of all systems during warranty period.

Provide one replacement media for the water filtration unit.

Provide a test set complete with apparatus and chemical reagents for the determination of appropriate control test, including chloride, pH and any additional test as required by Water Treatment company.

9.	PRODUCTS

9.1	Chemical Materials

Materials

System Cleaner:

Liquid alkaline compound with emulsifying agents and detergents to remove grease and petroleum products; sodium tripoly phosphate and sodium molybdate.

Algaecide; chlorine release agents such as sodium hypochlorite or calcium hypochlorite, or microbiocides such as quarternary ammonia compounds, tributyl tin oxide, methylene bis (thiocyanate), or isothiazolones.

Closed System Treatment (Chilled Water and Hot Water):

Sequestering agent to reduce deposits and adjust pH; polyphosphate.

Corrosion inhibitors; boron-nitrite, sodium nitrite and borax, sodium totyltriazole, low molecular weight polymers, phosphonates, sodium molybdate, or sulphites.

Conductivity enhancers; phosphates or phosphonates.

Condenser Water System Treatment (Cooling Towers):

Sequestering agent to inhibit scaling; phosphonates, sodium polyphosphates, lignin derivatives, synthetic polymer polyelectrolytes, or organite phosphates.

Acid to reduce alkalinity and pH.

Corrosion inhibitor; zinc-phosphate, phosponate-phosphate, phosphonate-molybdate and phosphonate-silicate, sodium tolyltriazole, or low molecular weight polymers.

Algaecide; chlorine release agents such as sodium hypochlorite or calcium hypochlorite, or microbiocides such as quarternary ammonia compounds, tributyl tin oxide, methylene bis (thiocyanate), or isothiazolones.

10	Chemical Feed Systems and Metering Pumps

General: Provide completely pre-assemble packaged chemical feed system. Package shall be hydraulically and electrically tested at the factory.  Package shall be furnished with all required lubricants, special tools, and installation instructions.

Pump

Pump capacity shall be adjustable through 100% of the range by manual micrometer dial while the pump is running or stopped.  Pump stroking speed shall not exceed 60 spm.  All parts of the power train must operate submerged in oil.

The pump shall be sized to deliver the required capacity at 85% of maximum stroke length. Stroke adjustment shall be variable oil by-pass type mechanism, with the plunger powered through its entire travel.

The pump shall include an automatic vent and refill mechanism on the hydraulic side, which operates once each stroke.  The pump shall have an external hydraulic relief valve which is adjustable.

Double ball check valves shall be provided on the discharge to ensure accurate repeatable metering. The pump valves shall be removable for cleaning or replacement without the need to disturb suction or discharge piping.

The pump shall be field convertible to automatic stroke adjustment without the use of special tools, and without the need to replace any major frame parts.

The pump shall be furnished with a factory-mounted driver suitably sized for continuous operation at the maximum relief setting.  The motor shall be integrally mounted direct coupled.  No belts or pulleys should be used in the drive train or for capacity adjustment.

The pump shall be able to deliver a flow at least 5 l/hr at 16 bar.

Tank: The tank shall be constructed of polyethylene and furnished with a hinged or removable cover. Tank shall include connections for pump suction, drain, level gauge, chemical fill, dilution water, and relief valve return piping.  Drain connection shall be separate from pump suction connection.  Drain shall be located in the bottom of the tank.  Suction outlet connection shall be on the side wall of the tank, a minimum of 50 mm above the bottom.  Tank shall be furnished with level gauge and level switch. Liquid level switch shall be polyprophene housing with integrally mounted PVC air trap, receptacles for connection to metering pump and low level alarm.

Agitator: An angle plate mounted agitator with 304 stainless steal shaft and propeller shall be furnished. The mixer propeller shall operate at 1750 rpm.  The purpose of the agitator shall be to maintain chemicals in homogenous suspension or solution.

11	Equipment

By-pass (Pot) Feeder: Fifteen gallon capacity. Include inlet and outlet connections, drain connections, level gauge sight glass with guards and 150 mm diameter feeding funnel, all valves, half inch sample valves and support legs.

Drip Feeder: Plastic reservoir with coil of capillary tubing with probe, weight, charging syringe, and clip.

Conductivity Controller: Packaged monitor controller with solid state circuiting, five percent accuracy, linear dial adjustment, built-in calibration switch, on-off switch and light, control function light, output to control circuit and recorder.

Water Meter:  Displacement type cold water meter with sealed, tamper-proof magnetic drive, impulse contact register, single pole, double throw dry contact switch.

Solenoid Valves: Forged brass body globe pattern, normally open or closed as required, general purpose solenoid enclosure, and continuous duty coil.

Timers:  Electronic timers, infinitely adjustable over full range, 150 second and five minute range, mounted together in cabinet with hands-off automatic switches and status lights.

Coupon Racks

Provide a coupon rack to monitor corrosion rates. The coupon rack shall be of prefabricated PVC bypass assembly and shall include:

Four corrosion coupons tees

Four corrosion coupons with holders

Flow control valve

Strainer

Additional corrosion coupons shall be provided depending on desired frequency of evaluation which shall be 60 days.  Results shall be reported as mils per year with comments as to pitting erosion.

A 120V circuit shall be provided to a junction box adjacent to the cooling tower and the water treatment equipment indoors.  Provide controls transformers for meters, timers, solenoid valves, probes, etc. As required.

12	Test Equipment

Provide white enamel test cabinet with local and fluorescent light, capable of accommodating 4 10 ml zeroing titrating burettes and associated reagents.

Provide the following test kits:

Alkalinity titration test kit.

Chloride titration test kit.

Sulphite titration test kit.

Total hardness titration test kit.

Low phosphate test kit.

Conductivity bridge, range 0 - 10,000 microhms.

Creosol red pH slide complete with reagent.

Portable electronic conductivity meter.

High nitrite test kit.

13	EXECUTION

13.1	Preparation

Carry out complete water chemical analysis to confirm applicable treatment type and chemicals required.

Remove all pipe caps and flange plates from headers and drain legs and remove all deposits from the systems. Ensure all strainers are clean and in place.

Systems shall be operational, filled, started, and vented prior to cleaning. Use water meter to record capacity in each system.  Record in treatment report.

Place terminal control valves in open position during cleaning. Where flushing and cleaning bypasses are provided ensure flushing and cleaning for the terminal devices and control valves is carried out separately to the remainder of the system. Do not flush general system through control valves, heat exchanges, coils, etc.

13.2	Cleaning Sequence

Add non-foaming chemical detergent cleaner compatible with all system components and materials to closed systems at concentration recommended by manufacturer.

Chilled Water Systems:  Circulate for 48 hours, then drain systems as quickly as possible.  Refill with clean water, circulate for 24 hours, then drain. Refill with clean water and repeat until system cleaner is removed.  The draining of the flush water need to be collected in temporary effluent tanks and taken away to be discharged as per local municipality requirement.

Use neutralizer agents on recommendation of system cleaner supplier and approval of Owner/PMC.

Flush open systems with clean water for one hour minimum. Drain completely and refill. Remove, clean, and replace strainer screens. Inspect, remove sludge, and flush low points with clean water after cleaning process is completed. Include disassembly and reassembly of components as required.

13.3	Closed System Treatment

Provide one bypass feeder on each system.  Install isolating and drain valves and necessary piping.  Install around globe valve downstream of circulating pumps unless indicated otherwise.

Introduce closed system treatment through bypass feeder when required or indicated by test. Provide 20 mm water coupon rack around circulating pumps with space for test specimens. Provide chemicals as specified to maintain the following conditions in each closed water system:

WATER

PH 					7.0 – 9.0

Molybdate 				50-100 ppm

Nitrate 					500-700 ppm

Orthophosphate				5.0-7.5 ppm

System Controller

An automatic control system shall be provided using conductivity for surface blowdown and water meter activation for proportionate feed of treatment chemicals. Provide timer activated sampling with solenoid valve, balancing valve, and conductivity probe. Pipe to blowdown tank.

The controller shall be a NEMA 12 steel enclosure with gasketed door, viewing window, lockable hasp-type door latch and either plug-in receptacles or knockouts for conduit installation.

The controller shall have the following features and accessories for blowdown control :

LED bar graph readout display (micron/cm) , Spark-plug type sensor probe 600# WSP

Field calibration adjustment (internal), Adjustable sample interval (1/4 to 3 hours) and duration (1/2 to 10 minutes) timers (front panel , Electric solenoid or motor operated ball valve sized as function of boiler HP and pressure, HOA switch for the valve “Operate-Test” switch uses a fixed resistor to simulate the sensor, Adjustable hysteresis or dead-band (internal), High, low, normal conductance indicator lights (LED), High or low conductance alarm light (flash or stead switch).  Trip points are field adjustable. Flash or steady switch has a silence position switch, External alarm bell Recorder output 0-5 volts, Illuminated Legend “Valve Open”, whenever blow-down is occurring.

The controller shall have the following features and accessories for chemical feed:

Electrical contact head water meter sized as function of makeup. Solid state counter Solid state time,  Test switch, HOA Switch for chemical pump, Illuminated legend; “Feed”, when pump is activated

Positive displacement metering pump having the necessary pressure rating and discharge capacity to meet system requirements and polyethylene mixing tank.  Provide separate pump tank package for feed of oxygen scavenger to deaerator storage section and for feed of other chemicals to return condensate tank directly into boiler drum.

Activate solution pumps when feedwater pumps are running.

Provide 20 mm water coupon rack on each feedwater pump with space for test specimens. Provide liquid level switch in each solution tank to de-activate solution pump and agitator, and signal mechanical alarm system.

13.4	Installation

Install in accordance with manufacturer's instructions.

14	Condenser Water Systems (Cooling Towers)

Provide automatic condenser water control systems for corrosion inhibitor feed, blowdown and biocide feeds. Inhibitor application shall be make-up water meter activated, blowdown shall be conductivity activated, and biocide shall be make-up water meter fed with blowdown locked out to ensure biocide retention time.

Control systems shall incorporate solid state integrated circuits and digital LED displays, in NEMA-12 steel enclosure.  Provide gasketed and lockable door.

Base dissolved solids control on conductivity and include the following in the controllers:

LED digital readout display (microhm/cm).

Temperature compensated sensor probe adaptable to sample stream manifold.

High, low, normal conductance indicator lights (LED).

High or low conductance alarm light (flash or steady switch), trip points field adjustable. Flash or steady switch shall have silence position.

Illuminated legend shall indicate “ALARM” whenever alarm condition exists.

Hand-off-automatic switch for solenoid bleed valve.

Illuminated legend shall indicate “BLEED” when valve is operated.

Adjustable hysteresis or dead-band (internal).

Base inhibitor feed control on make-up volume and include the following in the controller:

Solid state counter (1-15 field selectable), Solid state timer (adjustable 1/4 to 5 minutes). Test switch.

Hand-off-automatic switch for chemical pump.

Illuminated legend shall indicate “FEED” when pump is activated.

Solid state lock-out timer (adjustable 1/4 to 3 hours) and indicator light. Lock-out timer shall deactivate the pump and activate alarm circuits.

Panel totalizer (amount of makeup), electro-mechanical type.

Biocide Programmer to Include:

24 hour timer with 14 day skip feature to permit activation any hour of the day.

Precision solid state bleed lock-out timer (0 -9 hours) and biocide pump timer (0 -2-1/4 hours), clock controlled.

Solid state alternator to enable the use of two different formulations.

Digital display of the time of day (24 hours).

LED display of day of week (14 days).

Fast and slow clock set controls (internal).

Battery back-up so clock is not disturbed by power outages, quartz timekeeping accuracy.

Hand-off-automatic switches for biocide pumps.

Illuminated legend shall indicate “BIOCIDE A” or “BIOCIDE B” when pump is activated.

Activate system on flow switch integral to panel.

Provide water meter on system make-up, wired to chemical feed control system.

Provide solution pumps to feed sequestering agent and corrosion inhibitor from solution tank into condenser water supply to tower.  Provide agitator as specified.

Provide conductivity controller to sample condenser water and operate solenoid bleed valve and piping to blowdown controller sampler wired to open when condensing water pump is operating.

Introduce algaecide to tower by continuous feed with solution pump or solenoid valve on tank (chlorine).

Provide liquid level switch in each solution tank to de-activate solution pump and agitator, and alarm bell.

Provide 20 mm water coupon rack around circulating pumps with space for 4 test specimens.

15	SPARE PARTS & TOOLS

Contractor shall include in the contract to procure and handover the following minimum quantity of the spare parts as per the list and / or that recommended by the manufacturer.  These spare parts shall be brand new and similar to the equipment / material being installed.

Chemical Feed Pump		: 1 No.

Pump Impeller 			: 1 No.

Pump Bearing			: 2 sets

Agitator Bearing			: 1 set

Solenoid Valves			: 1 set

Water Meter			: 1 set

Liquid level switch		: 1 set

Multiple test kits for		: 1 set

each chemical as specified

Chemicals			: Lot (for 6 months duration)

# C.26	OZONE SYSTEM

- AIR OZONE SYSTEM

1	SCOPE

The scope of this section consists of but is not necessarily limited to the following:

a.	Design, Manufacture and supply of duct mounted air ozone generators with associated sensors, controllers and accessories.

b.	All associated items herein to be supplied, delivered and installed.

c.	Provide specialist’s agencies representative’s services including coordination, start up and testing supervision.

d.	Testing, start-up and supervision training and providing necessary documentation for operation.

e.	Carry out performance test at site.

2	QUALITY ASSURANCE PROGRAMME

a.	The Ozone system shall be sized in accordance with the parameters indicated in the Basis of Design.  The system shall be Owner/PMCed to achieve results as recommended by OSHO and ACGIH.

b.	The air ozone system shall be a product of a manufacturer normally supplying this type of equipment and who can show evidence having completed at least two installations of sizes 2000 TR and above, operating successfully in hot and humid environment for two years or more.

- The ozone generator shall be ETL listed.

3	CAPACITY

The capacity of the ozone system shall be selected by the specialist manufacturer and approval from Owner/PMC-in-charge.

4	OZONE GENERATORS

a.	Ozone Generators shall be provided with the primary aim of achieving reduction in Volatile Organic Compounds (VOC), hydro carbon gases, and organic odors, in Indoor Environment. They shall also serve purpose of depleting and inhibiting growth and propagation of microbial organisms and microflora, commonly found in indoor environments, HVAC ducts, cooling coils and on air filters. VOC reduction shall be achieved by oxidation of VOC by ozone. Depletion of microbial colonies shall be achieved by inhibiting their growth and propagation.

b.	The aim is to ensure the VOC are kept below the TLV (Threshold Limit Value) for occupied areas, as recommended by OSHA and or ACGIH.

c.	The maximum residual concentration of ozone in the indoor environment shall not exceed 50 PPB (v/v). PPB is Parts Per Billion.

d.	Ozone Generators shall be provided where called for, with number of corona discharge plates as listed in the schedules.

e.	Ozone Generators shall be compact, self contained units, with all components factory mounted in one neat, compact package. The ‘K’ type mounted inside the duct.

f.	Parts of the generators in contact with air stream shall be kept to as minimum as required.

g.	Components in contact with air stream shall be enclosed in stainless steel casing 18 G thick, with sufficient stamped integral openings to allow adequate flow of air over the corona discharge plates.

h.	The generator plates shall be mounted on generator head fabricated out of materials that repel accumulation and formation of sediments by tar, nicotine and grease. This is an extremely important prerequisite to enhance the operational reliability and ease of maintenance of the generator plates.

i.	The generators shall be suitable for mounting on ducts with air flow in horizontal, vertical or angular directions.

j.	The generators shall operate effectively with air flow in either direction, that is left to right or vice versa in horizontal ducts, and top to bottom or vice versa in vertical ducts.

k.	Generators shall be electrically interlocked with motor of the air handling unit fan. This will prevent start of the generator unless the fan motor is energized.

l.	The generators shall be suitable for mounting inside the ducts. It shall be provided with flange suitable for mounting on a metal frame, to be installed inside the duct.

m.	Openings in the ducts shall be made with sheet metal shears or cutters. Metal saw or grinding machine shall not be used, except to make an initial cut to permit use of metal shear. This precaution is taken to prevent metal debris from falling into the ducts.

n.	When mounted on the supply air duct, it is absolutely important to ensure the chosen location does not have carry over moisture from cooling coil or humidifier, or any other moisture emitting device.

o.	Care should be taken to ensure the generator is mounted on a straight run of duct with steady flow of air. Installation on bends, elbows, transition pieces, or close to dampers is not recommended.

p.	Air filter (efficiency 80%) shall be provided in the duct to prevent particulate in the air stream from reaching the ozone generator.

q.	Generation of ozone shall be only by principles of corona discharge. Multiple numbers of corona discharge plates shall be used to provide the necessary quantity of ozone. All the corona discharge plates shall be housed in one common stainless steel enclosure.

r.	Only multiple plate type corona surfaces shall be used for ozone generation. Production density of ozone per sq inch (or sq cm) of surface area of corona surface shall be as low as possible. Rate of variation of production of ozone shall follow approximately the rate of variation of VOC in the indoor environment. This is in view to ensure residual level of ozone in the indoor environment remains low while ensuring residual VOC level also remains low.

s.	Annual type of corona or corona mounted outside the air stream with ozone tubed to the duct shall not be used.

t.	Ozone and VOC shall be detected in the same gaseous stream, and ozone production shall be in this stream. To ensure this, ozone generator shall be duct mounted type. Portable type and generators that produce ozone outside the HVAC air stream are not acceptable, as they do not meet this criteria.

u.	Use of ionizer, or activated carbon filters is not permitted.

v.	Ozone generators shall not require any consumable for its operation, except for use of electricity.

w.	The system shall not rely on initial or replacement of filters of any sort to remove odors and chemicals.

x.	The ozone generators shall be capable of operating on 220 to 240 Volts, single phase power supply, 50  Hz. They shall be properly grounded.

y.	Ease of maintenance is important consideration. They shall be manufactured to permit easy withdrawals and refitting on the ducts, with minimum use of tools of hardware to remove or refit the generators to the ducts.

5	SENSOR MODULE

a.	Regulation of IAQ device shall be automatically controlled by Auto VOC Sensor and Variable Load controller

b.	Sensor and Controller shall be rated for continuous operation.

c.	Sensor shall be suitable for mounting in space, duct, plenum, or process chamber. If not space mounted, it shall be provided with Air Aspiration enclosure. Sampling air shall be aspirated to the enclosure and released.

d.	The Sensor shall be factory calibrated to Isobutylene gas 100 PPM for full span and controlled clean air for zero span. Factory stamped calibration certificate with date of calibration shall be provided with each Sensor.

e.	The VOC Sensor shall be capable of detecting broad range of commonly occurring VOC in indoor applications. Each gas sensed is related by the sensor to its corresponding concentration value to isobutylene.

f.	The sensor shall provide 4 distinct signals, one each for Clean, Low, Medium and High levels of concentration of the polluting VOC. The Sensor shall have 5 LED displays to provide visual indicating for the 4 levels, and warm up phase. It shall be possible to field adjust the sensitivity of the sensor.

g.	The sensor shall provide 0 to 10 VDC stepped and 0 to 5 VDC proportional output, field selectable, for interface to Automated building Management System.

h.	In the event of power failure, or if the system is turned off, the Sensor shall retain the pre set sensitivity.

i.	The sensor shall be provided with potentiometers to adjust the 4 levels of pollution, independent of one another.

j.	The Sensor shall be suitable for operation in air stream of RH 45% to 65%.

k.	Factory supplied interconnecting cable shall be provided, for communication between Sensor and Load Controller.

6	VARIABLE LOAD CONTROLLER

a.   	Controller shall be solid state, mounted in rugged stainless steel enclosure.

b.	It shall be fully factory assembled. Field provided connections shall be limited to power wiring.

c.	The Controller shall be suitable for accepting signals from the Sensor. Based on the signals received, it shall provide variable output to operate IAQ devices.

d.	Input voltage to controller shall be 120 Volts, 1 Ph, 60 Hz or 220 to 240 Volts, 1 Ph, 50 Hz (Factory set). It shall be suitable for load rating of 10 Amps.

e.	Controller shall be provided with terminal block to connect incoming power, variable outgoing power, and for interlock to AHU motor or other air moving device, and to safety device such as high ozone cut out switch.

f.	The Controller shall be provided with receptacle to accept easy plug in cable connector, for communication to Sensor.

g.	Controller shall be provided with 3 Lamps to indicate Power On Automatic, Manual Bypass.

h.	Controller shall be provided with rocker switch to choose Automatic or Manual Mode of operation. In the Manual Bypass Mode, voltage output of the Controller shall be 100% of input voltage, regardless of the level of VOC.

i.	Cable connector between Controller and Sensor, length not less than 25ft (7.5 M) shall be factory provided (specify length if longer than 25 feet is required). This shall be complete with cables to provide power to Sensor and transfer signals for the different levels of VOC from Sensor to Controller.

7	OZONE CONCENTRATION SENSOR, MONITOR AND CUTOUT SWITCH

a.	Ozone concentration monitor cum sensor shall be provided for the occupied areas. At least one Monitor/Sensor shall be provided for generators in the AHU serving the area.

b.	The monitor shall be installed in a side stream duct and not in the main duct. This is to ensure the sensor element is not exposed to high velocity of air found typically in all HVAC ducts. This ensures accuracy of sensor readings, and prolongs life of the sensor element.

c.	Lowest detection of the monitor shall be down to 20 PPB (v) or 0.02 PPM (v).

d.	Visual display shall be provided on the outer case of the Monitor. This shall comprise series of at least 10 pilot indicating lights, 4 green, 3 yellow and 3 red. When illuminated, they indicate the concentration of ozone in the following order.

e.	First green: Always On. Indicates power is ON.

f.	Next 3 green lights: Concentration of 20, 30 and 40 PPB respectively.

g.	Three yellow lights: Concentration of 50, 70 and 80 PPB respectively.

h.	First red light: 100 PPB (Maximum specified by OSHA)

i.	Second and third red lights: 120 and 140 PPB respectively.

j.	The sensor, monitor and all components shall be mounted in one neat and compact case, suitable for wall mounting. The indicating lights shall be mounted on the cover of the case. All components shall be factory mounted.

k.	The monitor shall have electrical leads to provide an open contact. In the event concentration of ozone reaches the set alarm value, ‘Normally Close’ changes to ‘Normally Open’ position. This will be used to electrically cut out the ozone generator, when concentration reaches the set value.

l.	Additionally, it shall also have an audible alarm, which is activated if the concentration reaches the set level. Switch shall be provided on the case of the monitor, to turn off the alarm, at the option of the user.

m.	The alarm shall be factory set at 50 PPB. However, it shall be possible to change this setting in the field to any desired level.

n.	The monitor shall provide a linear 0 to 2 Volts DC output voltage, proportional to concentration of ozone. This will be interfaced with the BMS to record continuously concentration in PPB or PPM, and also to produce hard copy printouts. This will also enable shutting down the ozone generators through the BMS, if the set high level is reached.

o.	The monitor shall be capable of interfacing with BMS. Necessary transponders to enable this will be provided by others.

p.	It shall also be possible to set the high ozone cut out level through the BMS, and to shut down the ozone generators through BMS, in the event the set alarm is reached.

q.	The monitor shall be suitable for continuous operation.

r.	Input power source is 24 volts, DC, provided. Suitable adaptor for this shall be provided with the Monitor.

8	CARBON DI OXIDE SENSOR AND MONITOR

a.	CO2 monitor cum sensor shall be provided for the occupied areas.  Atleast one monitor/sensor shall be provided for generators in the AHU serving area.

b.	Lowest detection of the Monitor shall be down to 50PPM.

c.	Visual digital display shall be provided  on the outer case of the Monitor, if the monitor is surface.  This shall read CO2 level in PPM.

d.	The sensor, monitor and all components shall be mounted in one neat and compact case, suitable for wall or duct mounting.  The indicating lights shall be mounted on the cover of the case, if surface mounted.  All components shall be factory mounted.

e.	The monitor shall provide 4 to 20 milli amps or 0 to 10 volts DC output signal.

f.	The monitor shall be capable of interfacing with BMS through the output signal.  Necessary transponders to enable this will be provided by others.

g.	Motorized fresh air damper shall be modulated through the signal from the sensor.

h.	The monitor shall be suitable for continuous operation.

- COOLING TOWER OZONE SYSTEM

1	SCOPE

The scope of this section consists of but is not necessarily limited to the following:

a.	Design, Manufacture and supply of  cooling tower ozone system.

b.	All associated items herein to be supplied, delivered and installed.

c.	Provide manufacturer’s representative’s services including coordination, start up and testing supervision.

d.	Testing, start-up and supervision training and providing necessary documentation for operation.

e.	Carry out performance test at site.

2	QUALITY ASSURANCE PROGRAMME/SYSTEM SPECIFICATIONS

a.	The Ozone system shall be sized in accordance with the design parameters.  The system shall be Owner/PMCed to achieve results as recommended by OSHO and ACGIH.

b.	The air ozone system shall be a product of a manufacturer normally supplying this type of equipment and who can show evidence having completed at least two installations of sizes 2000 TR and above, operating successfully in hot and humid environment for two years or more.

c.	Condenser water system shall be provided with controlled and regulated system of ozone injection to achieve scale suppression on condenser tubes and condenser water piping, corrosion inhibition, and control of microbial growth in water and in drift air from cooling tower.

d.	Ozone treatment shall be a stand alone treatment, and shall not use any form of supplementary addition of any type of chemical.

e.	Cycles of Concentration of condenser water shall be not less than 17 based on conductivity of tower basin water, based on POSI  less than 0.20 for available make up water. The tower water POSI shall be maintained less than 1.0. POSI = Practical Ozone Scaling Index.

f.	Concentration of ozone in condenser water system shall be;

g.	In the tower basin:			0.10 to 0.25 PPM.

h.	Prior to entry to condenser:		0.10 to 0.15 PPM.

i.	At entry to tower to spray nozzles:	0.01 to 0.05 PPM

j.	Microbial and algae level in the tower basin shall not be greater than 1000CFU per milli liter.

k.	Corrosion in the system shall not be higher than : 0.3  Mil In per year for copper and 5 Mil In per year for steel.

3	OZONE GENERATOR

a.	Ozone generated shall be maximum concentration 2 TO 3% wt/wt in air, with air as feed gas. Oxygen as feed gas is not permissible, and shall not be used.

b.	Ozone generation and variation of ozone output shall be at constant frequency. Modulation of ozone by frequency variation is not permissible.

c.	The equipment is housed indoor. The ozone generator shall be skid mounted, integrally piped and wired with external connections for wiring and piping connection on site.

d.	Ozone generator shell shall be fabricated of SS316L consisting removable head, 1” thick acrylic view port for visual monitoring of corona, vertical cylindrical housing corona tubes of SS316L. Each cylinder shall be provided with tri-clamp nozzle for air inlet. All gasket shall be fabricated of silicone, hypalon or teflon. The generators shall have ports for air inlet, ozone outlet, condenser water inlet and outlet and drain. Dielectric tubes shall be fabricated of alumina glass, and metalized with aluminum by plasma coating, to provide high efficiency dielectric. Each tube shall be independently protected by a H.T fuse.

e.	All pipes in contact with ozone shall  be SS316L. All other devices in contact with ozone shall be SS316L, glass silicone, PVDF.

f.	All electrical component shall confirm to CSA, NEC and UL ratings. The generator shall be suitable for operation on 380V – 410V, 3 Ø 50 Hz. Power density shall not exceed 0.30 watts per sq.cm of effective dielectric surface area.

g.	Power supply unit transformers shall be dye type, class F insulated with high temperature cutout for each phase, suitable for operation in 104°F (40°C) ambient, with temperature rise not higher than 122°F (50°C).

h.	The PSU shall consist of the following components as a minimum, all factory wired, assembled and tested:

- 3 phase harmonic filter to minimize total harmonic distortion.

- Three phase isolating transformer.

- Three phase fully controlled rectifier with snubbers and MOV’s (Metal Oxide Varistors) on each side.

- DC filter bank.

- IGBT inverter assembly complete with snubbers.

- Medium frequency oscillating circuit with over current and over voltage protection.

- Medium frequency dry-type transformer.

i.	If operation is on medium frequency, each Power Supply Unit shall have frequency electronic protection consisting rectifiers or invertors over current protection, over voltage protection at the IGBT modules, and high voltage short circuit protection.

j.	The ozone generator shall be provided with emergency stop button with keyed lock out.

4	INSTRUMENTS, CONTROLS & VALVES

a.	Pneumatically operated spring assisted back flow preventor shall be provided on the ozone pipe to prevent reverse flow of injection water to the generator, and on the air flow line to prevent reverse flow of ozone to air pipes. They shall be located in the ozone generator cabinet and shall be factory piped.

b.	Air flow transmitter output with 4-20mA output and air flow rotameter shall be used to indicate volume of airflow.

c.	Outlet devices shall include high low air pressure safety shut down switch, pressure relief valve, ozone temperature sensor with high temperature safety shutdown, flow regulator valve, ozone sample valve, electrically operated solenoid valve, water flow rotameter, high water temperature safety shut down and low water flow switch on the cooling water circuit.

5	AUTOMATION, CONTROLS, AND SAFETY DEVICES

a.	Ozone generator shall be provided with motorized powerstat to allow automatic variation of ozone output from 10% to 100% of the full capacity.

b.	Ozone generator shall be provided with microprocessor controller.

c.	Side stream injection system shall be provided with ORP sensor and controller. Based on the ORP of the water sensed, it provides 4 to 20 Mil Amps signal to the microprocessor, which in turn modulates the generator. The ORP controller also provides visual digital readout of the ORP in Mil Volts.

d.	Conductive sensor and controller shall be provided in the Side stream piping. It shall provide 4 to 20 Mil Amps output. Based on set value of the conductivity, it automatically controls the electric solenoid valve on the blow down line of the cooling tower. Conductivity monitor also provides visual digital indication of conductivity in Micro Mho.

e.	Adjustable time delay device to delay start between compressor and generator. This is actuated by the microprocessor.

f.	Pneumatic solenoid valve mounted in series with back flow preventor valve to provide rapid and positive shut off in the ozone injection line.

g.	Ozone generator shall be provided with a port with shut off valve on the air intake stream, to enable the field installation contractor to provide compressed air to operate the pneumatic solenoid valve.

h.	High low level switch in the tower basin to regulate the rate of out flow of blow down water. This is not a factory supplied item, and shall be field provided by the installation contractor.

i.	All monitors shall provide 4 to 20 Mil Amps output which may be input to the BMS system, if used.

j.	Adequate electrical interlocks shall be provided between the air compressor, ozone generator, and injection water pump, as will be shown in the electrical circuit diagram.

k.	The system shall be designed for continuous operation, pre wired for modulating ozone output from between 10% and 100% of the maximum design output.

l.	Corrosion coupon rack with coupon holders for copper and steel shall be provided, with initial supply of coupons. It shall be complete with constant flow orifice device.

m.	Colorimeter and ampoules for high and low dissolved ozone concentration in water shall be provided.  Initial supply shall be at least 40 ampoules.

6	AIR COMPRESSOR

a.	Air compressor with ASTM receiver with pressure relief valve rated for continuous operation, sized to provide adequate air flow for generation of ozone with allowance for loss of air to purge the desiccant dryer and for reduction in volume experienced after removal of moisture. Compressor shall be reciprocating type (screw type of scroll).

b.	Air preparation package shall comprise prefilter to 1 micron, coalescent filter to 0.01 micron particle and 0.01 micron oil removal and after filter to 1 micron, and twin tower pressure swing heatless desiccant dryer for dryness to dew point temperature of -70°C as 90 PSIG. Quality of air should meet ISO 8573-1; clause 1.1.1.

7	INJECTION WATER SYSTEM

a.	Vertical loop method /venturi injector shall be used to inject produced ozone into the water stream. Side stream injection water shall be raised by a vertical loop to a point where the pressure in the water is lowered sufficient to allow injection of produced ozone into the water stream. Pressure gauges shall be provided at both ends of the vertical loop. Pneumatic, quick shut off valve and back flow preventor valves shall be provided in the ozone injection line to prevent reverse flow of water into the ozone generator.

b.	Injection of ozone into the water stream shall be by venturi injector. Pressure differential switch shall be provided to ensure the venturi develops the necessary pressure difference to inject ozone into the stream. In the event this is not achieved, the pressure differential switch shall shut down the pneumatic back flow preventor valve and the ozone generator to ensure injection water does not flow into the generator. Back pressure from the down steam of the venturi shall be adequate to return water to the tower basin and distribute the same in the basin.

c.	Injection water pump shall be close coupled, centrifugal pump, CI casing, steel shaft with SS 316 sleeve, bronze impeller, and EPDM seal.

d.	Commissioning and balancing of the system shall be done by factory-trained technicians.

8	PLANT CAPACITY

a.	Appropriate capacity of the generator shall be submitted by the specialist.

b.      	Side stream injection water pump shall be sized by the manufacturer and   submitted for approval.

c.	Air compressor: Same as above.

9	COMPLETION PHASE-I TEST AND PROVISIONAL TAKING OVER OF PLANT:

On completion of installation and commissioning of the plant, the following aspects shall meet with to the satisfaction of the Owner/PMC-in-charge:-

    - That the plant, equipment and accessories provided are mechanically sound and conform to the contract specifications.

    - That the finish and the general appearance of the work is as per the contract specifications.

    - That the design layout and workmanship are satisfactory.

    - Phase-I test: - This test shall be 24 hours continuous running test to be carried out by the contractor in presence of the Owner/PMC-in-charge. Time versus chilled water temperature graphs shall be plotted. The plant shall achieve the designed weather condition irrespective of any variation up to 50 % of the specified equipment and occupancy load. In case the occupancy and load conditions are not available at the time commissioning of AC plant artificial conditions shall be created to conduct this test. The artificial load shall be provided by the contractor.

- PHASE-II TEST AND GAURANTEE OF PERFORMANCE:

These tests shall be of 72 hours continuous running tests and shall be carried out when extreme summer, monsoon and winter conditions are available as follows:-

      - Summer/Hot Weather Test. This test shall be carried out in month of May/June.

      - Monsoon Test. This test shall be carried out in the month of July/August.

      - Winter Test. This test shall be carried out in the month of Dec/Jan.

  - The results of the tests shall be recorded in the required format here-in-after to the particular specifications. Phase II tests shall be carried out by the contractor in presence of the Owner/PMC-in-charge, within 12 months’ period following Phase-I test. In case at the time of initial commissioning of the plant, the extreme weather conditions as per the month specified for any of the phase-II test are occurring, phase –I test shall be combined with relevant Phase-II test.

  - The plant shall be finally taken over after satisfactory last seasonal phase-II test.

  - Each group of plants shall be tested independently. All compressor and condensing units shall be tested by operating these in rotation.

If any of the Phase I/Phase II does not show satisfactory results, the contractor shall at his own cost rectify/replace the defective installation or any part thereof as directed by the Owner/PMC-in-charge within three months. The decision of Owner/PMC-in-charge shall be final and binding in this respect. The installation shall be subjected to retest under the similar outdoor conditions, which if failed, (e.g. if the plant failed during Monsoon test, it shall be retested during monsoon only) after such rectification of defects again for 72 hours continuously and results recorded as done in previous tests. The installation shall be finally taken over after the contractor submits satisfactory phase-II tests as certified by the Owner/PMC-in-charge.

  - The contractor shall guarantee all items of equipment, electrical machinery & wiring etc. for period of Defect Liability period after successful completion of last seasonal phase-II test.

The designed inside temperature and all other temperature and humidity conditions specified in the tender shall be ensured during the above the period. The contractor shall be guarantee that the capacity of various components as well as the whole systems shall not be less than that specified in the tender. The maintenance of the plant shall also be responsibility of the contractor during the above period. Any spares/defects required to be attended during the above period shall be at the cost of the contractor.

- TRAINING OF Owner/PMC

The Contractor shall impart eight weeks training in running and maintenance of the installation to the Owner/PMC connected with the running of plant as detailed by the Owner/PMC-in-charge. This training shall be imparted after commissioning the plant and during/after phase-I testing for this purpose, the contractor’s representative shall remain on site even after phase-I test and provisional taking over, till the above period of training is complete.