## Sheet1
Item 1
Annual degradation - CCCL Infrastructure Ltd - Solar plant at tuticorin
Sl no | Particular | Units
1 | Maximum units generation as per NVVN for 5MW | 9198000
2 | Degradation at 0.8% p.a from April 2012 to Mar 2024- 12Years | 8352827 | 8352826.7019
Note
1) The Degradation factor should also consider the following
a) Guaranteed output committed by manufacturer which is 90% Guaranteed output for 10Years, 80% guaranteed output for 25 years.
b) Only five inverters of the installed ten inverters are functioning
c) Out of 12 No's Installed Breaker, 2No's Not Working
d) Solar Panel Out of 33,360 No's of (150Watt each) installed Capacity, nearly 1500 No's Panels Not Working
e) Torrentian rains and floods in the last couple of years
f) Harmonic issues in power transmission, which damaged performance of major solar equipments and which warranted shifting of substation connectivity.
Item 2
Auxillary consumption during the current financial year, for 11 month is 92880 units, 4.3%
Item 3
Details of actual MW in operation based on units generated
Mega Watt Reached
Sl.No | Financial Year | Total Export units against Total achievable 91,98,000 units for 5MW | MW in operation against commissioned 5MW | maximum output that can be generated | %plf
1 | 2018-2019 | 6940530 | 3.7 | 32412000 | 21.41%
2 | 2019-2020 | 6020370 | 3.2 | 28032000 | 21.48%
3 | 2020-2021 | 1668870 | 0.9 | 7884000 | 21.17%
4 | 2021-2022 | 3859920 | 2.09 | 18308400 | 21.08%
5 | 2022-2023 | 3594510 | 1.95 | 17082000 | 21.04%
6 | 2023-2024 | 2160810 | 1.17 | 10249200 | 21.08%