## Sheet1
| Particulars | Technical Spefications | Rated/ Installed Capacity | Installation date
Unit-1 | Generator | Make :SHANDONG JINAN POWER EQUIPMENT FACTORY THE PEOPLE’S REPUBLIC OF CHINA, Capacity: 50MW,Rated Voltage:11KV, Power factor:0.8PF,Speed:3000RPM,Frequency:50HZ | Capacity: 50MW,50Hz,0.8PF,11KV | Jun-June-2010
| Turbine | Make:QINGDAO JIENENG STEAM TURBINE GROUP CO.,LTD , Speed :3000RPM, Condensing Turbine, Inlet steam pressure : 88.3Kg/Sq.cm , Steam temperature :535 deg.C | MODEL N50-8.83, 50MW CONDENSING STEAM TURBINE | Jun-June-2010
| Boiler | Make: Sichuan Chuanguo Boiler Co., Ltd., Steaming capacity:230TPH, Type of Boiler : CFBC | Steam capacity:230TPH at 88.3 kg/sq.cm,535 deg.C | Jun-June-2010
| Cooling tower | Make: Gea cooling tower, No.of cells : 6 nos, Water circulation capacity:10,300Cub.M/hr, Water holding capaity:4000 Cub.M, Type: Induced draft, Approach: 5 | Water circulation capacity:10,300Cub.M/hr, In let cooling water temp:42 deg.C, and Out let cooling water temp:32 deg.C, | Jun-June-2010
| Transformer | Make: Vijay Electricals, Rated MVA : 80MVA, Voltage:11kv/132kv, Type of cooling : ONAF, Vector group: YNd1 | 80MVA, 11/132KV,ONAF | Jun-June-2010
| DM Plant | Make: Ion Exchange, RO Plant, Out put capacity:12 TPH | RO plant, output capacity:12 TPH | Jun-June-2010
Unit-2 | Generator | Make :BHEL,Hyderabad, Capacity: 50MW,Rated Voltage:11KV, Power factor:0.8PF,Speed:3000RPM,Frequency:50HZ | Capacity: 50MW,50Hz,0.8PF,11KV | March-2015
| Turbine | Make:BHEL , Speed :3000RPM, Inlet steam pressure : 105Kg/Sq.cm , Steam temperature :535 deg.C, Type of condenser: air cooled condenser | Power Output: 50MW, | March-2015
| Boiler | Make: ISGEC Heavy Engineering Limited, Steaming capacity:215TPH, Type of Boiler : CFBC | Steam capacity:215TPH at109kg/sq.cm,540 deg.C | March-2015
| Transformer | Make: Bharat bijlee, Rated MVA : 80MVA, Voltage:11kv/132kv, Type of cooling : ONAF, Vector group: YNd1 | 80MVA, 11/132KV,ONAF | March-2015