## Sheet1
Brief Details of Equipments at 1x63 MW TPP ACBIL Renki
Sl. No. | Name of Equipment | Quantity | Make | Capacity | Remarks
A | BTG
1 | CFBC Boiler | 1 | Wuxi Huanghang China | 250 TPH
2 | I D Fan with Drive | 2 | Flake wood | Fan:79(M3/SEC) Motor: 5850KW,6.6KV
3 | PA Fan with Drive | 2 | Flake wood | Fan:23.5(M3/SEC) Motor: 350KW,6.6KV
4 | SA Fan with Drive | 2 | Flake wood | Fan:28.5(M3/SEC) Motor: 750KW,6.6KV
5 | J- seal Fan | 3 | Kay international | Fan:3500(M3/SEC) Motor:75 KW,415V
6 | Steam Turbine (Non reheated) | 1 | Hangzhou steam Turbine Co.Ltd | Max continuous Output:-63 MW
7 | CEP with Drive | 2 | Zhejiang Pump General Works, China | Flow:300(M3/SEC) Motor capacity: 185kw,415V
8 | BFP with Drive | 2 | Zhe Jiang Shenke Slide Bearing co.ltd | Flow:334(M3/SEC) Motor capacity: 1900kw,6.6KV
9 | LUBE OIL SYSTEM | 1 | FIL+ SEP EQUIPMENT PVT LTD-India
i) | MOP with Drive | 1 | Zhe Jiang Pump General Works | Flow:135(M3/Hr) Motor capacity: 75kw,415V
ii) | AOP with Drive | 1 | Zhe Jiang Pump General Works | Flow:135(M3/Hr) Motor capacity: 75kw,415V
iii) | JOP with Drive | 1 | HIGH TECH FLUID POWER CO LTD | Flow:64.7(M3/Hr) Motor capacity: 30kw,415V
iv) | EOP(AC) with Drive | 1 | ZHE JIANG PUMP GENERAL WORKS | Flow:40(M3/Hr) Motor capacity: 7.5kw,415V
v) | EOP(DC) with Drive | 1 | ZHE JIANG PUMP GENERAL WORKS | Flow:40(M3/Hr) Motor capacity: 7.5kw,110VDC
vi) | Settling oil for Turbine Oil with Drive | 1 |  | Flow:1.2(M3/Hr) Motor capacity: 0.7kw,415V
vii) | Oil Purifier Device of Steaming Machine with Drive | 1 | Neng Jian (Jiang su) Machinery & power- generating eq. co.ltd | Motor capacity: 4.0kw,415V
10 | GSVC with Drive | 1 | Hangzhou steam turbine | Flow:853(M3/Hr) Motor capacity: 3.0kw,415V
11 | Vaccum Pump with Drive | 2 | Chinees | Flow:2200(M3/Hr) Motor capacity: 75kw,415V
12 | LP Heater | 2 | Nanjing turbine & electric machine grouping co.ltd | Flow:220(M2)
13 | HP Heater | 2 | Nanjing turbine & electric machine grouping co.ltd | Flow:280(M2)
14 | Deaerator | 1 | SAME SECTION VIII DIVISION 1&HEI | DESIGN PRESSURE:6.676KG/CM2
15 | Water cooled Condensor | 1 | HTC | Codensor surface-4200 Sqmm
16 | Generator with Auxilliaries | 1 | SHANDONG JINAN POWER EQUIPMENT FACTORY | Rated Power:70MW,11KV
17 | Generating Transformer | 1 | Bharat Bijlee | Rated Power:80MVA,11/138 KV
18 | Station Transformer | 1 | Emco Ltd | Rated Power:20MVA,132/6.9 KV
19 | Unit Auxilliary Transformer | 1 | Voltamp Transformer Ltd | Rated Power:12.5MVA,11/6.9 KV
20 | DCS Panel | 9 | Supcon | DCS-ECS 700
21 | Turbo superviosary Instrument system | 1 | Bentaly nevoda | Bentaly nevoda 3500
22 | TG Governing System | 1 | Woodward | Micronet
23 | Electrical Control and relay panel | 15 | ABB | Rated volt-132Kv system
24 | Battery Bank for emegency DC supply and Protection system | 4 | HBL | Rated volt-110V/1000AH
25 | UPS and battery | 2 | Hitachi | 20KVA with 120AH batteries
26 | Station Swithgear panels | 13 | ABB | Rated volt-6.6KV
27 | Unit Switchgear panels | 19 | ABB | Rated volt-6.6KV
28 | LT panels | 14 | Nitya Ltd | Rated volt-415V
29 | Distribution Transformers for auxilliaries | 10 | Voltamp Transformer Ltd | Rated Power:2.0MVA,6.6/415KV
30 | 132KV Switchyard Equipments
31 | CT's- | 12 | ABB | Rated volt-132Kv
32 | PT's- | 15 | ABB | Rated volt-132Kv
33 | SF6 Breakers- | 4 | ABB | Rated volt-132Kv
34 | Isolators- | 22 | ABB | Rated volt-132Kv
35 | Busbars-Main and Transfer bus | 2 | ABB | Doble Zebra
36 | Lightening arresters- | 12 | ABB | Rated volt-120Kv
37 | Associated cabels | 1 Lot
38 | AVR panel | 1 | ABB | Rated volt-58V,Current-15.8A
B | BOP
1 | Cooling water system | Nos
i) | CW with Drive | 2 | Pump : Flowmore verticle Pump | Capacity:12000(M3/Hr) Motor capacity: 1250kw/6.6KV
ii) | ACW with Drive | 2 | Pump : Flowmore verticle Pump | Capacity:15000(M3/Hr) Motor capacity: 275kw/6.6KV
iii) | Cooling tower Fans with drives | 5 | Paharpur cooling tower ltd | Motor capacity: 93kw/415V
2 | Compressor
i) | Instrument air compressor | 2 | Atlas capcos | Capacity:7.5 bar Motor capacity: 75kw/415V
ii) | Service air compressor | 3 | Elgi (2 Nos) | Capacity:30.7 M3/ min Motor capacity: 176kw/415V
|  |  | Atlas capcos(1 Nos) | Capacity:401 L/s Motor capacity: 132KW/415V
3 | ESP
i) | ESP | 1 | Sunyard, China | capacity: 414000m3/h
ii) | Silicon rectifire transfer | 12 | Hangzho Tianming electric co ltd | capacity: 72kv
iii) | ESP HEATERS |  | Zhejnang zheng yao environmental protection science & technology | capacity: 1kw
iv) | EMITTING MOTORS | 12 | Guamao reducer co ltd | capacity: 0.37kw
v) | Switchgear panels | 15 | Hangzho Tianming electric co ltd | Rated volt-415V
xi) | Collecting motors | 6 | Guamao reducer co ltd | capacity: 0.37kw
4 | CHP | 2 | Elemech | 215TPH
I) | Coal Bunkers | 1 |  | capacity: 850m3
II) | Primary Crusher Technical Data | 2 | Hyquip | capacity: 170 tph,Motor 160KW
III) | Secondary Crusher Technical Data | 2 | Hyquip | capacity: 220 tph,Motor 160KW
iv) | Secondary Screen | 2 | Elemech | capacity: 215tph,Motor 40 hp
V) | Conveyor Belt | 10 | Elemech
vi) | Vibrating Feeder 1B // 1A |  | Electromag devices p ltd | capacity: 125-250 TPH,Motor 1.5KW
vii) | Electromagnetic Separator | 2
viii) | Switchgear panels | 15 | C&S switchgears | Rated volt-415V
5 | DM Plant | 2 | TRIVENI ENGINEERING & INDUSTRIES LIMITED | capacity: 22 M3/hr,
i) | Cooling tower Makeup pumps | 2 | Mather+Platt | capacity: 300 M3/hr,,Motor 30 KW
ii) | Hot well Makeup Pump | 2 | Mather+Platt | capacity: 15 M3/hr,,Motor 5.5 KW
iii) | Boiler Fill Pump with drives | 2 | Mather+Platt | capacity: 20M3/hr,,Motor 18.5 KW
iv) | DM Make Up Pump | 2 | Mather+Platt | capacity: 30M3/hr,,Motor 7.5 KW
v) | Service Water Pump | 2 | Mather+Platt | capacity: 15M3/hr,,Motor 5.5 KW
vi) | Switchgear panels | 2 | C&S switchgears | Rated volt-415V
6 | RAW WATER PUMP HOUSE
i) | Raw water pump with drives | 2 | Flowmore Pump | capacity: 350M3/hr,,Motor 45 KW
ii) | Fire fighting disel pump (1 nos) | 2 | Flowmore Pump | capacity: 273M3/hr,,Motor 115 KW
iii) | Fire Fighting Pumps | 2 | Flowmore Pump | capacity: 273M3/hr,,Motor 110 KW
iv) | Jockey pump (2 nos) | 2 | Flowmore Pump | capacity: 25M3/hr,,Motor 15 KW
v) | Switchgear panels | 8 | C&S switchgears | Rated volt-415V
7 | AHP | 2 | INDURE/MACAWBER BK | CAPACITY 56 MT/ HOUR )
i) | FLY ASH SILO | 2 | INDURE PVT. LTD. | capacity: 500 m3/hr,,
ii) | Switchgear panels | 9 | C&S switchgears | Rated volt-415V
8 | Emergency Power Back up
i) | 500 KVA DG Set | 1 | POWERICA | capacity: 500 KVA, 415 V, 50 Hz
ii) | 250 KVA DG Set | 1 | POWERICA | capacity: 250 KVA, 415 V, 50 Hz