## Sheet1
Particulars | Technical Spefications |  | Rated/ Installed Capacity | Installation date
GENERATOR | 30000 KW, 37500 KVA, 11000 VOLTS, 1968 A, 1500 RPM, 50 HZ, 4 POLE, 3 PHASE, IP54, CACW., TC210, Make TDPS, Inst Qty: 01No. |  | 30 MW | 2007-02-27
GENERATOR TRANSFORMER | 37500 KVA, 11 KV/132 KV, 1970.6 AMP/164.2 AMP, 3 PH, 50 HZ, COOLING-ONAN/ONAF, V.G.-Ynyn0, Oil VOL.-23000 LTRS, %Z= 12.85 @ NORMAL TAP, ON-LOAD TAP CHANGER., Make: AREVA, Inst Qty.: 01 No |  | 37.5 MVA | 2007-02-27
Diesel generator | 304 KW, 450 HP, 380 KVA, 529 AMP, 415 VOLTS, 50 HZ, 1500 RPM, 0.80 PF,3 PH, 4 POLE, Model: CJ380DFP, Make: JACKSON Ltd., Inst Qty: 01No |  | 380KVA | 2007-02-27
AUXILIARY TRANSFORMER | 2500 KVA, 11 KV / 0.433 KV, 131.2 AMP/3333.4 AMP, 3 PH, 50 HZ, COOLING-ONAN, V.G.-Dyn11, Oil VOL.-1290 LTRS, %Z-6.83 @ NORMAL TAP, OFF-LOAD TAP CHANGER., Make: AREVA, Inst. Qty: 03 Nos |  | 2.5MVA | 2007-02-27
DISTRIBUTION TRANSFORMER | 7500 KVA, 11 KV / 33 KV, 393.6 AMPS/131.2 AMPS, 3 PH, 50 HZ, COOLING-ONAN/ONAF, V.G.-Ynyn0, Oil VOL.-5520 LTRS, %Z= 8.68@ NORMAL TAP, ON-LOAD TAP CHANGER., Make: AREVA, Inst qty: 01 No. |  | 7.5MVA | 2007-02-27
132KV Switchyard | 1) SF6 Circuit Breaker, 145KV, 3150A, Siemens & 132KV s/s equipments |  | - | 2007-02-27
Boiler Feed Pump MOTOR | Capacity: 660KW, 2973RPM, 11KV,40Amp,50Hz, model: TPC450F, Make: CG., Inst qty: 02 |  | 660KW | 2007-02-27
FD-FAN MOTOR | Capacity: 355KW, 1480RPM, 415V,586Amp,50Hz, model: M2BA355MLA4, Make: ABB, Inst qty: 02 |  | 355KW | 2007-02-27
ID-FAN MOTOR | Capacity: 110KW, 980RPM, 415V,188Amp,50Hz, model: ND315M, Make: CG, Inst qty: 02 |  | 110KW | 2007-02-27
PA-FAN MOTOR | Capacity: 160KW, 1485RPM, 415V, 267Amp,50Hz, model: ND315M, Make: CG, Inst qty: 02 |  | 160KW | 2007-02-27
ACW Pump Motor | Capacity: 75KW, 1475RPM, 415V, 132Amp,50Hz, model: HX280SMB4, Make: ABB, Inst qty: 02 |  | 75KW | 2007-02-27
CW Pump Motor | Capacity: 250KW, 989RPM, 415V, 432Amp,50Hz, model: M2BA355MLA6, Make: ABB, Inst qty: 03 |  | 250 KW | 2007-02-27
Cooling Tower Fan Motor | Capacity: 55KW, 1470RPM, 415V, 96Amp,50Hz, model: D250M, Make: ALSTOM, Inst qty: 04 |  | 55KW | 2007-02-27
UPS for DCS | Capacity: 2x35KVA, Battery Capacity-240 Ah, Number of Cell-180, Charging Voltage-405 V(Float) & 423 V(Normal), Battery Current-Charging-24A,Battery & Cell Voltage-315 V, IP-42, Make-DB Power, Battery make: HBL, 2V, 240AH, 180Nos |  | 2x35KVA | 2007-02-27
Station Battery & Charger | Float & Float Cum Boost Charger Type: 110V / 80 Ah, AC I/P : 415 V , 50 Hz, 3 Ph, DC O/P (F.C.B.C.):128V/40A&153V/90A,DC O/P (F.C.) : 128 V / 40 A, Make : Servilink Battery Charger |  | 450AH | 2007-02-27
Packaged Air conditioner | Packaged Air Conditioner, Cap 15TR,Model : DPUWSH1505, EVAP Fan Motor : 415 VAC, 50 Hz, 3-Ph, 3 HP, Compressor Motor : 415 VAC, 20 AMPS, 50 Hz, 3-Ph, Heater : 230 VAC, 50 Hz, 1-Ph, Refrigerants : R22, 18 KG., Make : VOLTAS LTD. , Inst qty: 07 |  | 15TR | 2007-02-27
Distributed Control System (DCS) | DCS model: SPPA-T3000, make: Siemens, Reduntant set of Automation server, Application server for Boiler & Turbine. |  | 1 set | 2007-02-27
ESP | Alstom Projets India. Ltd., OHTA 58/1150, Field: 04, Efficiency: 99.95% |  | 4 Field/ single path | 2007-02-27
PRIMARY AIR FAN | EFFICIENCY | 2 X 100% | 02 Nos. | 2007-02-27
| TYPE | CENTRIFUGAL
| MEDIUM | HOT AIR
| FLOW | 13.00 M3/SEC
| PRESSURE | 700 MMWC
| TEMPRETURE | 170 DEG C
| TYPE OF DRIVE | DIRECT COUPLED
| SPEED | 1480 RPM
Supplier: M/S CETHAR VESSELS (P) LTD. | CASING ORIENTATION | ACW-10
| MOTOR RATING | 132 KW/ 4 POLE
FORCED DRAFT FAN | EFFICIENCY | 2 X 50% | 02 Nos. | 2007-02-27
| TYPE | CENTRIFUGAL
| MEDIUM | AMBIENT AIR
| FLOW | 26.25 M3/SEC
| PRESSURE | 800 MMWC
| TEMPRETURE | 40 DEG C
| TYPE OF DRIVE | DIRECT COUPLED
| SPEED | 1480 RPM
Supplier: M/S CETHAR VESSELS (P) LTD. | CASING ORIENTATION | ACW-15
| MOTOR RATING | 315 KW/ 4 POLE
INDUCED DRAFT FAN | EFFICIENCY | 2 X 50% | 02 Nos. | 2007-02-27
| TYPE | CENTRIFUGAL
| MEDIUM | FLUE GAS
| FLOW | 38.00 M3/SEC
| PRESSURE | 200 MMWC
| TEMPRETURE | 140 DEG C
| TYPE OF DRIVE | DIRECT COUPLED
| SPEED | 980 RPM
Supplier: M/S CETHAR VESSELS (P) LTD. | CASING ORIENTATION | CW-5
| MOTOR RATING | 110 KW/ 6 POLE
DRAG CHAIN COAL FEEDER | TYPE | 1205032/34/35 | 08 Nos. | 2007-02-27
| GearBox SN. RO. | DW/11806 & CW/06982
| TYPE | NU4
| RATIO | 50
Supplier: H POWER ASSOCIATES | MAKE | SHANI GEARS LTD.
BOILER FEED PUMP | Model | MD 80-260/14 | 02 Nos. | 2007-02-27
| Type | Centrifugal POSITION- Horizontal NO. OF STAGES-14
| Head | 1265 MWC
| Rated Flow | 136 M3/HR
| Efficiency | 76%
| Speed | 2973
| Operating Temp | 145
Supplier: SULZER PUMPS INDIA LIMITED | Suction Pr. | 5 kg/cm2
| Discharge Pr. | 112.5 kg/cm2
TURBINE | TYPE | SST 300-C160-1 FRAME-2.5 | 01 No. | 2007-02-27
| NO | 3.20.06.081 YEAR OF CONST: 2006
| POWER | 30000 KW
| SPEED | 7059 RPM
| PR. INLET | 84.00 ATA
| TEMP. INLET | 510.0 DEG C
| PR. BLEED 1 | 0.841 ATA
| TEMP. BLEED 1 | 94.34 DEG C
| PR. BLEED 2 | 4.405 ATA
| TEMP. BLEED 2 | 168 DEG C
| PR. EXTRACTION | 17.763 ATA
| TEMP. EXTRACTION | 313.3 DEG C
Supplier: SIEMENS LTD. | PR. EXHAUST | 0.113 ATA
| TEMP. EXAHUST | 47.92 DEG C
TURBINE GEAR BOX | UNIT | NF 3419 D | 01 No. | 2007-02-27
| ORDER | 352277
| SR. NO | 30-6215
| POWER | 31800 KW
| SPEED INPUT | 7064.5 RPM
Supplier: LUFKIN | SPEED OUTPUT | 1500 RPM
| GEAR RATIO | 4.7097
LP (LOW PRESSURE) HEATER | DRAWING NO | VO-05-3866/GA-LP | 01 No, | 2007-02-27
| TUBE SIZE | OD 15 mm X 2.0 mm thk X 53507442 (ST. LENGTH)
| TUBE PITCH/TYPE | 21mm / TRIANGULAR
| NO. OF TUBES | PROVIDED 204 'U'
| DESCRIPTION | SHELL SIDE
| DESIGN PR. KG/CM2(g) | 35 & FULL VACCUM
| HYDRO TEST PR. KG/CM2 (g) | 4.5
| DESIGN TEMP DEG C | 150
| TEST TEMP DEG C | AMBIENT
| CORROSION ALLOWANCE mm | 3.2
| NO. OF PASSES/ZONE | 2 ZONES
| FLUID | STEAM
| DESCRIPTION | TUBE SIDE
| DESIGN PR. KG/CM2(g) | 25
| HYDRO TEST PR. KG/CM2 (g) | 32.5
| DESIGN TEMP DEG C | 150
| TEST TEMP DEG C | AMBIENT
| CORROSION ALLOWANCE mm | 3.2
Supplier: MAZDA LIMITED | NO. OF PASSES/ZONE | 4 PASS
| FLUID | CONDENSATE
HP (HIGH PRESSURE) HEATER | DRAWING NO | VO-05-3866/GA-HP | 01 No, | 2007-02-27
| TUBE SIZE | OD 16mm X 1.5mm thk X 7550 (ST. LENGTH)
| TUBE LENGTH | 7550 STRAIGHT LENGTH
| TUBE PITCH/TYPE | 21mm / TRIANGULAR
| NO. OF TUBES | PROVIDED 156 'U'
| DESCRIPTION | SHELL SIDE
| DESIGN PR. KG/CM2(A) | 25 & FULL VACCUM
| TEST PR. KG/CM2 (A) | 37.5
| DESIGN TEMP DEG C | 377/225 (SKIRT/SHELL)
| TEST TEMP DEG C | AMBIENT
| CORROSION ALLOWANCE mm | 3.2
| STRESS RELIEVING | NO
| NO. OF PASSES | 1
| FLUID | STEAM & DRAINS
| DESCRIPTION | TUBE SIDE
| DESIGN PR. KG/CM2(A) | 160
| TEST PR. KG/CM2 (A) | 240
| DESIGN TEMP DEG C | 245
| TEST TEMP DEG C | AMBIENT
Supplier: MAZDA LIMITED | CORROSION ALLOWANCE mm | 3.2
| STRESS RELIEVING | YES
| NO. OF PASSES | 2
| FLUID | FEED WATER
TURBINE - CIRCULAR SURFACE CONDENSER | TYPE | RNE 23.0-2TSS 75 | 01 No. | 2007-02-27
| SURFACE OF CONDENSER (SQ MTR) | 1699
| CLEANLINESS FACTOR | 85%
| NO. OF PASSES | 2
| STEAM PRESSURE BAR ABS | 0.1106
| EXHAUST STEAM FLOW KG/SEC | 25.09
| EXHAUST STEAM ENTHALPY KJ/KG | 2310.9
| SATURATED STEAM TEMP DEG C | 47.79
| ENTHALPY OF CONDENSER KJ/KG | 200.1
| HEAT FLOW RATE KW/(K*SQMRT) | 3.146
| TRMINAL TEMP. DIFFERENCE (TDT) DEG C | 5.65
| COOLING WATER MASS FLOW RATE KG/SEC | 1285
| COOLING WATER VELOCITY M/S | 2.19
| COOLING WATER I/L TEMP. DEG C | 32
| COOLING WATER O/L TEMP. DEG C | 42.14
| CONDENSER DUTY KW | 52960
| SALINITY | 0%
| PR DROP (BAR) | 0.43
| TUBES NOS. | 3136
Supplier: DESEIN INDIA PVT. LTD. | TUBE OUTSIDE DIA mm | 23
| TUBE THK mm | 0.7
TURBINE EJECTOR SYSTEM | TYPE | TWO STAGE TWIN ELEMENT EJECTOR SYSTEM | 01 No. | 2007-02-27
| EXHAUST STEAM FLOW | TPH 87.88
| CONDENSING PRESSURE | ATA 0.113
| CONDENSATE TEMP. | DEG C 47.92
Supplier: NEW FIELD INDUSTRIAL EQUIPMENT PVT. LTD. | ENTHAPLY (KCAL/KG) | DEG C 552.2
INSTRUMENT AIR COMPRESSOR | MODEL: | EE75/9 | 03 Nos. | 2007-02-27
| CAPACITY | 14.53 m³ PER MIN
| MOTOR: | 75 KW
Supplier: ELGI | PR. | 8.16 KG/CM2
SERVICE AIR COMPRESSOR | MODEL: | EE75/9 | 02 Nos. | 2007-02-27
| CAPACITY | 14.53 m³ PER MIN
| MOTOR: | 75 KW
Supplier: ELGI | PR. | 8.16 KG/CM2
SERVICE AIR COMPRESSOR | MODEL: | E 45-7.5 | 01 Nos. | 2007-02-27
| CAPACITY | 8.49 m³ PER MIN
| MOTOR: | 45 KW
Supplier: ELGI | FAB. NO. | BMISO40641
SERVICE AIR COMPRESSOR | TYPE | GA-132 | 01 Nos. | 2007-02-27
| Motor Power | 132 KW
| Free Air Delivery | 401 Ltr/Sec
Supplier: Atlas Copco | Max. Final Pr. | 7.5 Bar
CONDENSATE EXTRACTION PUMP | Type | WKT 125/5 | 02 Nos. | 2007-02-27
| Drg. No. | F 051070001-2
| Head | 111 M
Supplier: KSB PUMPS LTD | FLOW | 115 M3/HR
| Speed | 1475
CIRCULATING COOLING WATER PUMP | Model | SDA 350/450 | 03 Nos. | 2007-02-27
| SL. No. | 9000209/210/213
| Head | 25 Mwc
| Capacity | 2500 m3/hr
| Input | 250 KW
Supplier: BEACON WEIR; UNIGLIDE PUMP, TYPE SD - HORIZONTAL | efficiency | 88.5%
| Speed | 975
COOLING TOWER FAN | FAN SR.NO. | 0.6.5.89 | 04 Nos. | 2007-02-27
| NO. OF BLADE | 8
| BLADE MATERIAL | RAINFORCED POLYSTER
| SERIES | 301
| SERIES (COOLING TOWER FAN GEAR REDUCER) | 32.2
| RATIO (COOLING TOWER FAN GEAR REDUCER) | 11.18/1
Supplier: PAHARPUR COOLING TOWER LTD. | MODEL (COOLING TOWER FAN GEAR REDUCER) | P 84 4123-1
| SR.NO. (COOLING TOWER FAN GEAR REDUCER) | D-6-591
AUXILLARY COOLING WATER PUMP | Model | SDCB 150/200 | 02 Nos. | 2007-02-27
| SL. No. | W0126205/W0126305
| Head | 40 MWC
| Capacity | 400 M3/HR
| Input | 75 KW
Supplier: BEACON WEIR; UNIGLIDE PUMP, TYPE SD - HORIZONTAL, Chennai -IND | efficiency | 88%
| Speed | 1480
CIRCULATING COOLING WATER PUMP | Model | SDA 350/450 | 02 Nos. | 2007-02-27
| SL. No. | 9000209/210/213
| Head | 25 Mwc
| Capacity | 2500 m3/hr
| Input | 250 KW
Supplier: BEACON WEIR; UNIGLIDE PUMP, TYPE SD - HORIZONTAL | efficiency | 88.5%
| Speed | 975
BOILER FILL PUMP | Model | CNW 80/250 | 02 Nos. | 2007-02-27
| SL. No. | W0126405/W0126505
| Head | 80 M
| Capacity | 45 m³/hr
| Input | 22 KW
Supplier: BEACON WEIR PROCESS PUMP | Efficiency | 60%
| Speed | 2930 rpm
DEAREATOR MAKEUP | Model | FNB 13 STAGE | 02 Nos. | 2007-02-27
| SL. No. | W0149405/505
| Head | 90 Mwc
| Capacity | 1.94 LPS = 6.98 m3/hr
| Input | 3.7 KW
Supplier: Beacon Weir SPIROGLIDE PUMP; TYPE F - HORIZONTAL | Efficiency | 57%
| Speed | 1430 rpm
FIRE FIGHTING MAIN | Type | DB 100/25 | 01 No. | 2007-02-27
| O/A NO. | 0786 A 199 W/0800
| Head | 70 M
| Capacity | 171 M3/Hr
Supplier: KIRLOSKAR BROTHERS LTD | Input | 47.24 KW
| Speed | 2900
FIRE FIGHTING JOCKEY PUMP | Type | DB 32/36 | 01 No. | 2007-02-27
| O/A NO. | 0786 A 136 W/1000
| Head | 470 M
| Capacity | 10.8 M3/Hr
Supplier: KIRLOSKAR BROTHERS LTD | Input | 7.35 KW
| Speed | 2900
FIRE FIGHTING D.G. PUMP | Type | C 100/40 | 01 No. | 2007-02-27
| O/A NO. | 07A5 A 3500/0100
| Head | 80 M
| Capacity | 171 M3/Hr
Supplier: KIRLOSKAR BROTHERS LTD | Input | 47.24 KW
JACKWELL - SPIT CASING PUMP | Type | UP 125/30 A | 03 Nos. | 2007-02-27
| NO. | 1747106066
| Head | 20 M
| Capacity | 252 M3/Hr
Supplier: KIRLOSKAR BROTHERS LTD | Input | 16.72 KW
| Speed | 1440
CLARIFIRE | 10000 DIA x 4500 SWD REACTOR CLARIFIER WITH NF-18 LT DRIVE HEAD |  | 01 No. | 2007-02-27
| ORDER NO | PXD-537
| ORDER DATE | 23-07-2005
GEARBOX DETAILS
| O.NO. | 9334.5
| TYPE | 337
| RATIO | 701 R11
Supplier: TRIVENI ENGINEERING & INDUSTRIES LTD. | SR.NO. | SR3717
| MAKE | PRIUM ENERY TRANSMISSION LTD
CRUSHER | CAPACITY | 50 TPH | 01 No. | 2007-02-27
| TYPE MODEL | BW RG 60 100
| MOTOR | 50 HP
| SPEED | 1440 RPM
Supplier: BEVCON WAYORS P LTD | EFFICIENCY | 85%
FLIP FLOW SCREEN | CAPACITY | 125 TPH | 01 No. | 2007-02-27
| ORDER NO | 91117xM05
| SERIAL NO | S-023
Supplier: BEVCON WAYORS P LTD | YEAR | 2005
BELT CONVEYOR 3 | CAPACITY | 150 TPH | 01 No. | 2007-02-27
| LENGTH | 145 MTR
ELECON GEAR BOX TYPE-SFU RATIO-25:1 SERIAL NO-1004034 SIZE-12 INCH HANDLING -RH-HB-ACW
Supplier: ELECON | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 4 | CAPACITY | 120 TPH | 01 No. | 2007-02-27
| LENGTH | 148 MTR
ELECON GEAR BOX TYPE-SNU600 RATIO-40:1 SERIAL NO-491780 SIZE-7 INCH & GREAVES GEAR BOX TYPE U 700 RATIO 40:1 SL NO. - 2BF86646
Supplier: ELECON | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 5 | CAPACITY | 80 TPH | 01 No. | 2007-02-27
| LENGTH | 70 MTR
GREAVES GEAR BOX TYPE-U500 RATIO-30:1R SERIAL NO-2BF 87907 SIZE-5 INCH
Supplier: ELECON | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 650 MM WIDE - 4 PLY
BELT CONVEYOR 6 | CAPACITY | 120 TPH | 01 No. | 2007-02-27
| LENGTH | 162 MTR
GREAVES GEAR BOX TYPE-U500 RATIO-30:1R SERIAL NO-2BF 87907 SIZE-5 INCH
Supplier: ELECON | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 7 | CAPACITY | 120 TPH | 01 No. | 2007-02-27
| LENGTH | 16 MTR
GREAVES GEAR BOX TYPE-U500 RATIO-30:1R SERIAL NO-495175 SIZE - 5 INCH
Supplier: ELECON | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 1000 MM WIDE - 4 PLY