## Sheet1
Particulars | Technical Spefications |  | Rated/ Installed Capacity | Installation date
GENERATOR | 30000 KW, 37500 KVA, 11000 VOLTS, 1968 A, 1500 RPM, 50 HZ, 4 POLE, 3 PHASE, IP54, CACW., TC210, Make TDPS, Inst Qty: 01No. |  | 30 MW | 2014-03-27
GENERATOR TRANSFORMER | 37500 KVA, 11 KV/132 KV, 1970.6 AMP/164.2 AMP, 3 PH, 50 HZ, COOLING-ONAN/ONAF, V.G.-Ynyn0, Oil VOL.-23000 LTRS, %Z= 12.85 @ NORMAL TAP, ON-LOAD TAP CHANGER., Make: VOLTAMPS, Inst Qty.: 01 No |  | 37.5 MVA | 2014-03-27
Diesel generator | 400 KW, 450 HP, 500 KVA, 695 AMP, 415 VOLTS, 50 HZ, 1500 RPM, 0.80 PF,3 PH, 4 POLE, Model: CJ380DFP, Make: Sterline., Inst Qty: 01No |  | 500KVA | 2014-03-27
AUXILIARY TRANSFORMER | 2500 KVA, 11 KV / 0.433 KV, 131.2 AMP/3333.4 AMP, 3 PH, 50 HZ, COOLING-ONAN, V.G.-Dyn11, Oil VOL.-1290 LTRS, %Z-6.83 @ NORMAL TAP, OFF-LOAD TAP CHANGER., Make: VOLTAMPS, Inst. Qty: 02 Nos |  | 2.5MVA | 2014-03-27
132KV Switchyard | 1) SF6 Circuit Breaker, 145KV, 3150A, Siemens & 132KV s/s equipments |  | - | 2014-03-27
Boiler Feed Pump MOTOR | Capacity: 850KW, 2977RPM, 11KV, 54Amp,50Hz, model: AMI450L2A, Make: ABB., Inst qty: 02 |  | 850 KW | 2014-03-27
PA- FAN MOTOR | Capacity: 400KW, 1492RPM, 11KV, 25Amp,50Hz, model: TPC-450E, Make: CG, Inst qty: 02 |  | 400 KW | 2014-03-27
ID-FAN MOTOR | Capacity: 250KW, 1482RPM, 11KV,17Amp,50Hz, model: TPC-400E, Make: CG, Inst qty: 02 |  | 250KW | 2014-03-27
SA-FAN MOTOR | Capacity: 160KW, 1485RPM, 415V, 267Amp,50Hz, model: ND315LX, Make: CG, Inst qty: 02 |  | 160KW | 2014-03-27
ACW Pump Motor | Capacity: 160KW, 1485RPM, 415V, 272Amp,50Hz, model: D315LA, Make: Marathon, Inst qty: 02 |  | 160KW | 2014-03-27
Cooling water Pump Motor | Capacity: 315KW, 989RPM, 11KV, 22.5Amp,50Hz, model: DC450U900, Make: Marathon, Inst qty: 03 |  | 315KW | 2014-03-27
Cooling Tower Fan Motor | Capacity: 75/15KW, 1485/738RPM, 415V, 128/36Amp,50Hz, model: D280M, Make: Marathon, Inst qty: 03 |  | 75 KW | 2014-03-27
UPS for DCS | 2x20KVA UPS (30MW-New),Emerson Network, model: Leibert Hipulse D, UPS#1: Sr. No: 213US6319001. UPS#2: Sr. No: 213US6319002. I/L: 415VAC,42A, 3Ph, 50Hz. O/L: 230VAC,87A, 1Ph, 50Hz. Battery: 240V DC |  | 2x20KVA | 2014-03-27
Station Battery & Charger | Type: Two float cum boost with DCDB and DCSP, Flaot: 125V/70A, Boost: 152V/140A, 415V, Make: Servelink engineers pvt. Ltd., Sr. No: JN-1089 |  | 700AH | 2014-03-27
Packaged Air conditioner | Cap 5TR, Motor : 415 VAC, 50 Hz, 3-Ph, Make : BLUESTAR, Inst qty: 05 |  | 5TR | 2014-03-27
Distributed Control System (DCS) | Wave Field: ECS-100, Make: SUPCON |  | 1 set | 2014-03-27
ESP | Thermax Ltd., Model: TEI, Field: 05, Efficiency: 99.93% |  | 5 fields/ single path | 2014-03-27
PRIMARY AIR FAN | Fan model | 2140-SI-BAB-11 | 02 Nos. | 2014-03-27
| Flow | 17.03 m3/sec
| Static Pressure at Fan Outlet | 1738.02 mmWc
| Inlet pressure loss due to silencer & IGV or System | -25 mmWc
| Total Static Pressure develop | -25 mmWc
| Dynamic Head | 24.46 mmWc
| Normal speed at 50 HZ | 1480 rpm
| Minimum Speed at 47.5 HZ | 1425 rpm
| Maximum Speed at 51.5 HZ | 1545 rpm
| Vriable speed at different load condition | 1425 rpm
Supplier: Andrew Yule & Co Ltd | Static efficiency | 81.7 %
| Shaft Power at 1425 rpm | 341.3 Kw
SECONDARY AIR FAN | Fan model | 1720-SI-BAB-11 | 02 Nos. | 2014-03-27
| Flow | 10.25 m3/sec
| Static Pressure at Fan Outlet | 1054.03 mmWc
| Inlet pressure loss due to silencer & IGV or System | -20 mmWc
| Total Static Pressure develop | 1074.03 mmWc
| Dynamic Head | 24.46 mmWc
| Normal speed at 50 HZ | 1480 rpm
| Minimum Speed at 47.5 HZ | 1425 rpm
| Maximum Speed at 51.5 HZ | 1545 rpm
| Vriable speed at different load condition | 1425 rpm
Supplier: Andrew Yule & Co Ltd | Static efficiency | 82.12 %
| Shaft Power at 1425 rpm | 127.1 Kw
INDUCED DRAFT FAN | Fan model | 1595-SI-BCB-92 | 02 Nos. | 2014-03-27
| Flow | 39.79 m3/sec
| Static Pressure at Fan Outlet | 0 mmWc
| Inlet pressure loss due to silencer & IGV or System | -427.78 mmWc
| Total Static Pressure develop | 427.78 mmWc
| Dynamic Head | 24.46 mmWc
| Normal speed at 50 HZ | 1480 rpm
| Minimum Speed at 47.5 HZ | 1425 rpm
| Maximum Speed at 51.5 HZ | 1545 rpm
| Vriable speed at different load condition | 1425 rpm
Supplier: Andrew Yule & Co Ltd | Static efficiency | 82.55 %
| Shaft Power at 1425 rpm | 199.24 Kw
BOOSTER FAN / LOOP SEAL BLOWER | Model | RM - 290 AC | 02 Nos. | 2014-03-27
| P.O. NO. | OCS/SP/PO/12-13/012 DTD 31.08.2012
| Capacity | 2130 M3/HR
| Pressure | 3211 MWC
| Blower Operating Speed | 1200
Supplier: SWAM ROTARY BLOWER | MOTOR SPEED | 45/1500 KW/RPM
COAL FEEDER | FACTORY SR.NO. | 1205032/34/35 | 03 Nos. | 2014-03-27
| FEEDING MIDDLE DISTANCE | 6000 mm
| WEIGHING PRECISION | BETTER THAN ± 0.5%
| SWEEPER POWER | 1.5 KW 415VAC
| PRODUCTION DATE | 2012.5
Supplier: XUZHOU HUANENG MEASURE & CONTROL ELECTRIC EQUIPEMENT CO. LTD. (CHINA) | MAXIMUM FEEDING RATE | ICS-30 A
| CONVEYOR POWER | 4 KW 415 VAC
| FEEDER SPEED | 1440 RPM
| MODE OF OPERATION | VFD
BOILER FEED PUMP | Type | HGC 4/09 | 02 Nos. | 2014-03-27
| SL. No. | 9972161882-100/200
| Head | 1361.8 m
| Rated Flow | 164.80 m3/hr
| Q min | 52/ thermal, 67/continous
| Efficiency | 73%
| Nominal Speed | 2950
| effective Speed | 2982
| Operating Temp | 153.2 deg
| Suction Pr. | 6.26 kg/cm2
| Diff. Pr. | 124.47 kg/cm2
Supplier: KSB PUMPS LTD | Discharge Pr. | 130.73 kg/cm2
| cooling water Pr. | 3-4 kg/cm2
TURBINE | TYPE | SST 300 (C2L/V56AB) | 01 No. | 2014-03-27
| NO | 3.20.12.336 YEAR: 2013
| POWER | 30000 KW
| SPEED | 6000 RPM
| PR. INLET | 84.00 ATA
| TEMP. INLET | 515.0 DEG C
| PR. BLEED 1 | 1.28 ATA
| TEMP. BLEED 1 | 106.2 DEG C
| PR. BLEED 2 | 5.75 ATA
| TEMP. BLEED 2 | 191.8 DEG C
| PR. BLEED 3 | 17.87 ATA
| TEMP. BLEED 3 | 312.4 DEG C
| PR. EXHAUST | 0.09 ATA
Supplier: SIEMENS LTD. | TEMP. EXAHUST | 43.41 DEG C
HP (HIGH PRESSURE) HEATER | DRAWING NO | VO-12-8784/GA-HP | 01 No. | 2014-03-27
| TUBE SIZE | OD 5/8" X 1.24 thk X 7120 (ST. LENGTH)
| TUBE LENGTH | 7550 STRAIGHT LENGTH
| TUBE PITCH/TYPE | 21mm / TRIANGULAR
| NO. OF TUBES | PROVIDED 200 'U'
| DESCRIPTION | SHELL SIDE
| DESIGN PR. KG/CM2(A) | 22
| TEST PR. KG/CM2 (A) | 33
| DESIGN TEMP DEG C | 340/240 (SKIRT/SHELL)
| TEST TEMP DEG C | AMBIENT
| CORROSION ALLOWANCE mm | 3.2
| STRESS RELIEVING | NO
| NO. OF PASSES/ZONE | THREE ZONES
| FLUID | STEAM & DRAINS
| DESCRIPTION | CHANNEL SIDE
| DESIGN PR. KG/CM2(A) | 147.6
| TEST PR. KG/CM2 (A) | 221.5
| DESIGN TEMP DEG C | 240
| TEST TEMP DEG C | AMBIENT
| CORROSION ALLOWANCE mm | 3.2
Supplier: MAZDA LIMITED | STRESS RELIEVING | YES
| FLUID | FEED WATER
LP (LOW PRESSURE) HEATER | DRAWING NO | VO-12-8784/GA-LP | 01 No. | 2014-03-27
| TUBE SIZE | OD 5/8" X 20WBG X 4815 (ST. LENGTH)
| TUBE PITCH/TYPE | 21mm / TRIANGULAR
| NO. OF TUBES | PROVIDED 206 'U'
| DESCRIPTION | SHELL SIDE
| DESIGN PR. KG/CM2(g) | 1.6
| HYDRO TEST PR. KG/CM2 (g) | 2.4
| DESIGN TEMP DEG C | 130
| TEST TEMP DEG C | AMBIENT
| CORROSION ALLOWANCE mm | 3.2
| NO. OF PASSES | 1
| NO. OF ZONE | TWO
| FLUID | STEAM
| DESCRIPTION | TUBE SIDE
| DESIGN PR. KG/CM2(g) | 16
| HYDRO TEST PR. KG/CM2 (g) | 24
| DESIGN TEMP DEG C | 130
| TEST TEMP DEG C | AMBIENT
| CORROSION ALLOWANCE mm | 3.2
Supplier: MAZDA LIMITED | NO. OF PASSES | 4
| FLUID | CONDENSATE
TURBINE - SURFACE CONDENSER | DOCUMENT NO | E01400011 | 01 Nos. | 2014-03-27
| TYPE | SINGLE PRESSURE, TWO PASS, DEVIDED TYPE, AXIAL CIRCULAR SURFACE CONDENSER
| WBS NO. | TWBS 0060
| CONDENSER SURFACE AREA | 2536 sq. m
| CLEANLINESS FACTOR | 85%
| NO. OF PASSES | 2
| PLUGGING MARGINE | 10%
| COLING WATER VELOCITY | 2.25 m/s
| PR DROP | <0.8 BAR
| TUBES NOS. | 6528
| TUBE OUTSIDE DIA | 19.05 mm
Supplier: SIMENS/ AQUATHERM ENGG CONSULTANCY P. LTD. | TUBE THK | 0.7mm
| HOTWELL VOLUME | 8.5 MTR CUBE (APPROX)
TURBINE GENERATOR GEAR BOX | F.G. JOB NO. | 4657237.2 | 01 No. | 2014-03-27
| TYPE | TX80/4C
| SR. NO. | N 11931
| SIZE | TX 80/4C
| SR. NO. | NFQ 11931
GEAR DATA
| GEAR RATED | 32670 KW
| SERVICE FACTOR | AGMA 6011-i03≥
| RATED INPUT SPEED | 16347 RPM
| RATED OUTPUT SPEED | 1500 RPM
| SPEED RATIO | 4.03
| NO. OF TEETH GEAR/PINION | 129/32
CONSTRUCTION FEATURES
| CENTERLINES DISTANCE | 810 mm
| TOTAL WEIGHT | 15050 KG
| UPPER CASING TOTAL WT. | 1750 KG
| LOWER CASING TOTAL WT. | 13250 KG
| HIGH SPEED SHAFT WT. | 669.4 KG
| LOW SPEED SHAFT WT. | 6555.3 KG
LUBRICATION
| LUBE OIL | 46 ISO VG
| FILTERING | 25 MICRONS
| INLET PR. | 15 BARG
| NORMAL OIL I/L TEMP. | 50 DEG C
| MAX. OIL I/L TEMP. | 60 DG C
| OIL FLOW | 577 l/mn
Supplier: FLENDER | CALORIES TO EVACUATE | 386517 kCal/h
TURBINE EJECTOR SYSTEM | DRAWING NO | 20/E/2731/1 | 01 Nos. | 2014-03-27
| SUCTION PR (ata) | 0.033
| SUCTION TEMP | 45.5 DEG C
| SUCTION FLOW W.V (kg/hr) | 33.75
| SUCTION FLOW AIR (kg/hr) | 15.33
| MOTIVE STEAM PR (ATA) | 12/10 (NOR/MIN)
| MOTIVE STEAM TEMP (DEG C) | 400/350 (NOR/MIN)
| MOTIVE STEAM CONS. (TOTAL) (kg/hr) | 253/264 (NOR/MIN)
| STEAM CONS. FOR HOGGER (kg/hr) | 400/416 (NOR/MIN)
Supplier: AQUATHERM ENGG CONSULTANCY P. LTD. | WEIGHT EMPTY (SYSTEM) (kgs) | 3200
| FULL OF WATER (SYSTEM) (kgs) | 3800
CONDENSATE EXTRACTION PUMP | Type | WKT 100/02 | 01 No. | 2014-03-27
| SL. No. | 9972192322/100, 200
| Head | 140
| Capacity | 117 m³/hr
| P | 751 A
| Efficiency | 71%
Supplier: KSB PUMPS LTD | Speed | 2978 rpm
INSTRUMENT AIR COMPRESSOR | SR.NO. | SCR0001130 | 03 Nos. | 2014-03-27
| MODEL NO | KES 37-8.5 C
| CAPACITY | 6.48 M3/MIN
| WORKING PR | 8.0 BAR G
| COMP. BLOCK SPEC. NO. | 2730127 BD
Supplier: KRILOSKAR | COMP. BLOCK SR. NO. | 37-8.5-025/024/023
SERVICE AIR COMPRESSOR | MODEL: | E 110 | 03 Nos. | 2014-03-27
| MOTOR: | 110 KW
Supplier: ELGI | PRESSURE | 14 BAR (g)
AUXILLARY COOLING WATER PUMP | Model | CNW 300/500 | 02 Nos. | 2014-03-27
| SL. No. | W0040312/ 40212
| Head | 53
| Capacity | 750 m³/hr
Supplier: BEST & CROMPTON ENGG. LTD | Input | 1370 KW/HR
| Speed | 1485 rpm
CIRCULATING COOLING WATER PUMP | Model | SDA 16/20 B | 03 Nos. | 2014-03-27
| SL. No. | W0043312/ 43212/ 43112
| Head | 28
| Capacity | 3200 m³/hr
| Input | 274.17 KW/HP
Supplier: BEST & CROMPTON ENGG. LTD | efficiency | 89%
| Speed | 989 rpm
DEAREATOR MAKEUP PUMP | Model | FNB 4 | 02 Nos. | 2014-03-27
| SL. No. | W0040112/ 40012
| Head | 95
| Capacity | 6 m³/hr
| Input | 4.2 KW/HR
| Efficiency | 37%
Supplier: Beacon Weir | Speed | 2850 rpm
Boiler fill Pump | Model | CNW 80/200 | 01 No. | 2014-03-27
| SL. No. | W0038612
| Head | 47
| Capacity | 60 m³/hr
| Input | 10.82 KW/HR
Supplier: BEST & CROMPTON ENGG. LTD | Efficiency | 71%
| Speed | 2880 rpm
COOLING TOWER FAN | FAN SR.NO. | S-14-XL-6A-121 | 03 Nos. | 2014-03-27
| NO. OF BLADE | 8
| BLADE MATERIAL | RAINFORCED POLYSTER
| SERIES | 301
| SERIES (COOLING TOWER FAN GEAR REDUCER) | 32.2
| RATIO (COOLING TOWER FAN GEAR REDUCER) | 12.93-1
Supplier: PAHARPUR COOLING TOWER LTD. | MODEL (COOLING TOWER FAN GEAR REDUCER) | P 84-5424-2
| SR.NO. (COOLING TOWER FAN GEAR REDUCER) | US13J5-26
CRUSHER | CAPACITY | 150 TPH | 01 No. | 2014-03-27
| TYPE MODEL | IMPACTOR
| EQUIPMENT NO | 010-1047
Supplier: ACCT | EQUIPMENT SIZE | APS 1313
FLIP FLOW SCREEN | CAPACITY | 250 TPH | 01 No. | 2014-03-27
Supplier: ACCT | ORDER NO | PD-85
BELT CONVEYOR 8 | CAPACITY | 150 TPH | 01 No. | 2014-03-27
| LENGTH | 15 MTR
ELECON GEAR BOX TYPE-SNU RATIO-25:1R SERIAL NO-699013 SIZE - 5 INCH
Supplier: ACCT | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 9 | CAPACITY | 150 TPH | 01 No. | 2014-03-27
| LENGTH | 95 MTR
ELECON GEAR BOX TYPE-SNU RATIO-25:1R SERIAL NO-1054428 SIZE - 7 INCH
Supplier: ACCT | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 9A | CAPACITY | 150 TPH | 01 No. | 2014-03-27
| LENGTH | 85 MTR
Shanti gears Type- FU8 Ratio- 30 Sl.no. - AW/07365
Supplier: ACCT | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 10 | CAPACITY | 150 TPH | 01 No. | 2014-03-27
| LENGTH | 309 MTR
ELECON GEAR BOX TYPE-SFU RATIO-25:1 SERIAL NO-1004033 SIZE-12 INCH HANDLING -RH-HB-ACW
Supplier: ACCT | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 10A | CAPACITY | 150 TPH | 01 No. | 2014-03-27
| LENGTH | 50 MTR
PREMIUM GEAR BOX TYPE-SNU600 RATIO-25:1R SERIAL NO-2BF156660 SIZE - 5 INCH
Supplier: ACCT | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY
BELT CONVEYOR 11 | CAPACITY | 150 TPH | 01 No. | 2014-03-27
| LENGTH | 18 MTR
ELECON GEAR BOX TYPE-SNU RATIO-25:1R SERIAL no.- 699014 SIZE - 5 INCH
Supplier: ACCT | NN 800/4 - 4 PLY -4x2 MM NYLON RUBBER GRD M 24 | 800 MM WIDE - 4 PLY